## base_values
Name | Value
Base_MVA

## bus
Bus ID | GSP Group | BSP Group | Bus Name | If Slack | V_nominal (kV) | V_min (pu) | V_max (pu) | V_angle_min (rad) | V_angle_max (rad) | Geo_lon | Geo_lat
1 | Kearsley |  | kearsley_GSP | 1 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3588 | 53.5391
2 | Kearsley |  | agecroft_1 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2975 | 53.5128
3 | Kearsley |  | agecroft_2 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2975 | 53.5128
4 | Kearsley |  | atherton_1 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5123 | 53.514
5 | Kearsley |  | atherton_2 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5123 | 53.514
6 | Kearsley |  | bolton_1 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4206 | 53.591
7 | Kearsley |  | bolton_2 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4206 | 53.591
8 | Kearsley |  | bury_1 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2997 | 53.5967
9 | Kearsley |  | bury_2 | 0 | 132 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2997 | 53.5967
10 | Kearsley |  | agecroft_BSP | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2975 | 53.5128
11 | Kearsley |  | atherton_BSP | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5123 | 53.514
12 | Kearsley |  | bolton_BSP | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4206 | 53.591
13 | Kearsley |  | bury_BSP | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2997 | 53.5967
14 | Kearsley | Agecroft | cheetham_hill | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2488 | 53.5163
15 | Kearsley | Agecroft | clifton_junction | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3141 | 53.5237
16 | Kearsley | Agecroft | prestwich | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.282 | 53.5323
17 | Kearsley | Agecroft | swinton | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3277 | 53.5117
18 | Kearsley | Agecroft | the_height_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3063 | 53.5008
19 | Kearsley | Agecroft | the_height_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3063 | 53.5008
20 | Kearsley | Atherton | atherton_town_centre_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4917 | 53.5255
21 | Kearsley | Atherton | atherton_town_centre_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4917 | 53.5255
22 | Kearsley | Atherton | bedford | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5103 | 53.4946
23 | Kearsley | Atherton | hindley_green | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5539 | 53.5248
24 | Kearsley | Atherton | kirkhall_lane_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5215 | 53.5053
25 | Kearsley | Atherton | kirkhall_lane_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5215 | 53.5053
26 | Kearsley | Atherton | leigh | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5158 | 53.4947
27 | Kearsley | Bolton | barbara_st | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.444 | 53.5642
28 | Kearsley | Bolton | bradshawgate_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4258 | 53.5759
29 | Kearsley | Bolton | bradshawgate_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4258 | 53.5759
30 | Kearsley | Bolton | cox_green | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4263 | 53.6187
31 | Kearsley | Bolton | harwood | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3934 | 53.5944
32 | Kearsley | Bolton | musgrave_rd | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4542 | 53.5844
33 | Kearsley | Bolton | spa_rd_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4383 | 53.5779
34 | Kearsley | Bolton | spa_rd_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4383 | 53.5779
35 | Kearsley | Bolton | union_rd_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4216 | 53.5912
36 | Kearsley | Bolton | union_rd_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4216 | 53.5912
37 | Kearsley | Bolton | wordsworth_st_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4439 | 53.5937
38 | Kearsley | Bolton | wordsworth_st_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4439 | 53.5937
39 | Kearsley | Bury | bury_town_centre_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2909 | 53.5934
40 | Kearsley | Bury | bury_town_centre_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2909 | 53.5934
41 | Kearsley | Bury | dumers_lane | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3029 | 53.5696
42 | Kearsley | Bury | heap_bridge | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2614 | 53.59
43 | Kearsley | Bury | holt_st | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3244 | 53.6434
44 | Kearsley | Bury | woolfold_1 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3205 | 53.6013
45 | Kearsley | Bury | woolfold_2 | 0 | 33 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3205 | 53.6013
46 | Kearsley | Agecroft | cheetham_hill_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2488 | 53.5163
47 | Kearsley | Agecroft | clifton_junction_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3141 | 53.5237
48 | Kearsley | Agecroft | prestwich_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.282 | 53.5323
49 | Kearsley | Agecroft | swinton_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3277 | 53.5117
50 | Kearsley | Agecroft | the_height_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3063 | 53.5008
51 | Kearsley | Atherton | atherton_town_centre_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4917 | 53.5255
52 | Kearsley | Atherton | bedford_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5103 | 53.4946
53 | Kearsley | Atherton | hindley_green_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5539 | 53.5248
54 | Kearsley | Atherton | kirkhall_lane_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5215 | 53.5053
55 | Kearsley | Atherton | leigh_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.5158 | 53.4947
56 | Kearsley | Bolton | barbara_st_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.444 | 53.5642
57 | Kearsley | Bolton | bradshawgate_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4258 | 53.5759
58 | Kearsley | Bolton | cox_green_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4263 | 53.6187
59 | Kearsley | Bolton | harwood_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3934 | 53.5944
60 | Kearsley | Bolton | musgrave_rd_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4542 | 53.5844
61 | Kearsley | Bolton | spa_rd_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4383 | 53.5779
62 | Kearsley | Bolton | union_rd_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4216 | 53.5912
63 | Kearsley | Bolton | wordsworth_st_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.4439 | 53.5937
64 | Kearsley | Bury | bury_town_centre_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2909 | 53.5934
65 | Kearsley | Bury | dumers_lane_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3029 | 53.5696
66 | Kearsley | Bury | heap_bridge_PS | 0 | 6.6 | 0.95 | 1.05 | -0.5 | 0.5 | -2.2614 | 53.59
67 | Kearsley | Bury | holt_st_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3244 | 53.6434
68 | Kearsley | Bury | woolfold_PS | 0 | 11 | 0.95 | 1.05 | -0.5 | 0.5 | -2.3205 | 53.6013

## line&trafo
From_bus ID | From_bus Name | To_bus ID | To_bus Name | V_from (kV) | V_to (kV) | Type (1 for line, 0 for transformer) | If Hardenable | Length (km) | Resistance (pu) | Reactance (pu) | Thermal Rating (Amp) | S_max (MW) | P_max (MW)
1 | kearsley_GSP | 2 | agecroft_1 | 132 | 132 | 1 | 1 | 6.206 | 0.00040322 | 0.00097587 | 573 | 131.0054 | 131.0054
1 | kearsley_GSP | 3 | agecroft_2 | 132 | 132 | 1 | 1 | 7.042 | 0.00051057 | 0.0013586 | 573 | 131.0054 | 131.0054
1 | kearsley_GSP | 4 | atherton_1 | 132 | 132 | 1 | 1 | 13.63 | 0.000346 | 0.002657 | 815 | 186.334 | 186.334
1 | kearsley_GSP | 5 | atherton_2 | 132 | 132 | 1 | 1 | 13.63 | 0.000357 | 0.002536 | 815 | 186.334 | 186.334
1 | kearsley_GSP | 6 | bolton_1 | 132 | 132 | 1 | 1 | 10.34 | 0.0003668 | 0.0017756 | 866 | 197.9942 | 197.9942
1 | kearsley_GSP | 7 | bolton_2 | 132 | 132 | 1 | 1 | 10.28 | 0.00036596 | 0.0017808 | 866 | 197.9942 | 197.9942
1 | kearsley_GSP | 8 | bury_1 | 132 | 132 | 1 | 1 | 8.36 | 0.00035147 | 0.001761 | 428.6388 | 98 | 98
1 | kearsley_GSP | 9 | bury_2 | 132 | 132 | 1 | 1 | 8.51 | 0.00035957 | 0.00178 | 428.6388 | 98 | 98
2 | agecroft_1 | 10 | agecroft_BSP | 132 | 33 | 0 | 0 | 0 | 0.0010395 | 0.028947 |  | 60 | 60
3 | agecroft_2 | 10 | agecroft_BSP | 132 | 33 | 0 | 0 | 0 | 0.0010626 | 0.028846 |  | 60 | 60
4 | atherton_1 | 11 | atherton_BSP | 132 | 33 | 0 | 0 | 0 | 0.0007734 | 0.023264 |  | 90 | 90
5 | atherton_2 | 11 | atherton_BSP | 132 | 33 | 0 | 0 | 0 | 0.0007827 | 0.023209 |  | 90 | 90
6 | bolton_1 | 12 | bolton_BSP | 132 | 33 | 0 | 0 | 0 | 0.0005691 | 0.028 |  | 90 | 90
7 | bolton_2 | 12 | bolton_BSP | 132 | 33 | 0 | 0 | 0 | 0.0005691 | 0.028 |  | 90 | 90
8 | bury_1 | 13 | bury_BSP | 132 | 33 | 0 | 0 | 0 | 0.0008185 | 0.02532 |  | 90 | 90
9 | bury_2 | 13 | bury_BSP | 132 | 33 | 0 | 0 | 0 | 0.0008296 | 0.025097 |  | 90 | 90
10 | agecroft_BSP | 14 | cheetham_hill | 33 | 33 | 1 | 1 | 5.7843 | 0.0054778 | 0.0047663 | 310 | 17.7189 | 17.7189
10 | agecroft_BSP | 15 | clifton_junction | 33 | 33 | 1 | 1 | 0.95 | 0.0008996 | 0.0007828 | 356 | 20.3481 | 20.3481
10 | agecroft_BSP | 16 | prestwich | 33 | 33 | 1 | 1 | 3.1292 | 0.0019063 | 0.0028081 | 435 | 24.8636 | 24.8636
10 | agecroft_BSP | 17 | swinton | 33 | 33 | 1 | 1 | 3.5167 | 0.0032923 | 0.0030852 | 356 | 20.3481 | 20.3481
10 | agecroft_BSP | 18 | the_height_1 | 33 | 33 | 1 | 1 | 2.1812 | 0.0030764 | 0.0019488 | 250 | 14.2894 | 14.2894
10 | agecroft_BSP | 19 | the_height_2 | 33 | 33 | 1 | 1 | 2.1882 | 0.0030852 | 0.0019548 | 250 | 14.2894 | 14.2894
11 | atherton_BSP | 20 | atherton_town_centre_1 | 33 | 33 | 1 | 1 | 2.2576 | 0.0018363 | 0.0016323 | 476 | 27.2071 | 27.2071
11 | atherton_BSP | 21 | atherton_town_centre_2 | 33 | 33 | 1 | 1 | 2.5233 | 0.001483 | 0.0025257 | 670 | 38.2956 | 38.2956
11 | atherton_BSP | 22 | bedford | 33 | 33 | 1 | 1 | 2.9552 | 0.0027986 | 0.0024351 | 400 | 22.8631 | 22.8631
11 | atherton_BSP | 23 | hindley_green | 33 | 33 | 1 | 1 | 4.27 | 0.0061243 | 0.005805 | 245 | 14.0036 | 14.0036
11 | atherton_BSP | 24 | kirkhall_lane_1 | 33 | 33 | 1 | 1 | 1.3246 | 0.0018268 | 0.001196 | 245 | 14.0036 | 14.0036
11 | atherton_BSP | 25 | kirkhall_lane_2 | 33 | 33 | 1 | 1 | 1.3198 | 0.0013187 | 0.0011877 | 356 | 20.3481 | 20.3481
11 | atherton_BSP | 26 | leigh | 33 | 33 | 1 | 1 | 2.6663 | 0.0023896 | 0.0028647 | 362 | 20.6911 | 20.6911
12 | bolton_BSP | 27 | barbara_st | 33 | 33 | 1 | 1 | 5.0938 | 0.0058382 | 0.0043529 | 235 | 13.4321 | 13.4321
12 | bolton_BSP | 28 | bradshawgate_1 | 33 | 33 | 1 | 1 | 3 | 0.0035143 | 0.0027158 | 263 | 15.0325 | 15.0325
12 | bolton_BSP | 29 | bradshawgate_2 | 33 | 33 | 1 | 1 | 2.5844 | 0.0020028 | 0.0018625 | 476 | 27.2071 | 27.2071
12 | bolton_BSP | 30 | cox_green | 33 | 33 | 1 | 1 | 5.0222 | 0.0059276 | 0.0053171 | 245 | 14.0036 | 14.0036
12 | bolton_BSP | 31 | harwood | 33 | 33 | 1 | 1 | 2.7841 | 0.001965 | 0.0019935 | 245 | 14.0036 | 14.0036
12 | bolton_BSP | 32 | musgrave_rd | 33 | 33 | 1 | 1 | 3.114 | 0.0029672 | 0.0025924 | 356 | 20.3481 | 20.3481
12 | bolton_BSP | 33 | spa_rd_1 | 33 | 33 | 1 | 1 | 2.391 | 0.0012504 | 0.0022604 | 356 | 20.3481 | 20.3481
12 | bolton_BSP | 34 | spa_rd_2 | 33 | 33 | 1 | 1 | 2.508 | 0.0013104 | 0.0023718 | 356 | 20.3481 | 20.3481
12 | bolton_BSP | 35 | union_rd_1 | 33 | 33 | 1 | 1 | 0.138 | 0.0001412 | 0.000129 | 356 | 20.3481 | 20.3481
12 | bolton_BSP | 36 | union_rd_2 | 33 | 33 | 1 | 1 | 0.146 | 0.0001494 | 0.0001365 | 356 | 20.3481 | 20.3481
12 | bolton_BSP | 37 | wordsworth_st_1 | 33 | 33 | 1 | 1 | 1.934 | 0.0013895 | 0.0013873 | 400 | 22.8631 | 22.8631
12 | bolton_BSP | 38 | wordsworth_st_2 | 33 | 33 | 1 | 1 | 3.441 | 0.0027682 | 0.002486 | 400 | 22.8631 | 22.8631
13 | bury_BSP | 39 | bury_town_centre_1 | 33 | 33 | 1 | 1 | 2.194 | 0.0014674 | 0.001553 | 492 | 28.1216 | 28.1216
13 | bury_BSP | 40 | bury_town_centre_2 | 33 | 33 | 1 | 1 | 1.051 | 0.0008308 | 0.0009175 | 400 | 22.8631 | 22.8631
13 | bury_BSP | 41 | dumers_lane | 33 | 33 | 1 | 1 | 3.7915 | 0.0030044 | 0.0027329 | 476 | 27.2071 | 27.2071
13 | bury_BSP | 42 | heap_bridge | 33 | 33 | 1 | 1 | 3.36 | 0.0022181 | 0.0028693 | 502 | 28.6932 | 28.6932
13 | bury_BSP | 43 | holt_st | 33 | 33 | 1 | 1 | 6.364 | 0.0077114 | 0.013052 | 356 | 20.3481 | 20.3481
13 | bury_BSP | 44 | woolfold_1 | 33 | 33 | 1 | 1 | 1.9395 | 0.0014435 | 0.0013882 | 476 | 27.2071 | 27.2071
13 | bury_BSP | 45 | woolfold_2 | 33 | 33 | 1 | 1 | 3.0897 | 0.0016758 | 0.001587 | 476 | 27.2071 | 27.2071
14 | cheetham_hill | 46 | cheetham_hill_PS | 33 | 6.6 | 0 | 0 | 0 | 0.001985 | 0.05826 |  | 23 | 23
15 | clifton_junction | 47 | clifton_junction_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.052 |  | 20 | 20
16 | prestwich | 48 | prestwich_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
17 | swinton | 49 | swinton_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
18 | the_height_1 | 50 | the_height_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
19 | the_height_2 | 50 | the_height_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
20 | atherton_town_centre_1 | 51 | atherton_town_centre_PS | 33 | 11 | 0 | 0 | 0 | 0.0015 | 0.035 |  | 38 | 38
21 | atherton_town_centre_2 | 51 | atherton_town_centre_PS | 33 | 11 | 0 | 0 | 0 | 0.0015 | 0.035 |  | 38 | 38
22 | bedford | 52 | bedford_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
23 | hindley_green | 53 | hindley_green_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 28
24 | kirkhall_lane_1 | 54 | kirkhall_lane_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 28
25 | kirkhall_lane_2 | 54 | kirkhall_lane_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 28
26 | leigh | 55 | leigh_PS | 33 | 11 | 0 | 0 | 0 | 0.00443 | 0.0576 |  | 23 | 23
27 | barbara_st | 56 | barbara_st_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.052 |  | 20 | 20
28 | bradshawgate_1 | 57 | bradshawgate_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.052 |  | 30 | 30
29 | bradshawgate_2 | 57 | bradshawgate_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.052 |  | 30 | 30
30 | cox_green | 58 | cox_green_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.052 |  | 28 | 28
31 | harwood | 59 | harwood_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.052 |  | 28 | 28
32 | musgrave_rd | 60 | musgrave_rd_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
33 | spa_rd_1 | 61 | spa_rd_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 30 | 30
34 | spa_rd_2 | 61 | spa_rd_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 30 | 30
35 | union_rd_1 | 62 | union_rd_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
36 | union_rd_2 | 62 | union_rd_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
37 | wordsworth_st_1 | 63 | wordsworth_st_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
38 | wordsworth_st_2 | 63 | wordsworth_st_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
39 | bury_town_centre_1 | 64 | bury_town_centre_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
40 | bury_town_centre_2 | 64 | bury_town_centre_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
41 | dumers_lane | 65 | dumers_lane_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 23 | 23
42 | heap_bridge | 66 | heap_bridge_PS | 33 | 6.6 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 28
43 | holt_st | 67 | holt_st_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 28
44 | woolfold_1 | 68 | woolfold_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 23
45 | woolfold_2 | 68 | woolfold_PS | 33 | 11 | 0 | 0 | 0 | 0.002 | 0.05 |  | 28 | 23

## load
Bus ID | Bus Name | DFES Name | Sd_max | Sd_min | Power Factor | Pd_max | Pd_min | Qd_max | Qd_min | Sd_max_original | Sd_min_original | Scale_Factor
10 | agecroft_BSP | Agecroft | 56.6911 | 15.1774 | 1 | 56.6911 | 15.1774 | 0 | 0 | 62.9901 | 15.1774 | 0.9
11 | atherton_BSP | Atherton | 72.7845 | 29.7311 | 1 | 72.7845 | 29.7311 | 0 | 0 | 80.8717 | 29.7311 | 0.9
12 | bolton_BSP | Bolton | 90.7866 | 28.2818 | 1 | 90.7866 | 28.2818 | 0 | 0 | 100.874 | 28.2818 | 0.9
13 | bury_BSP | Bury | 63.7423 | 16.4812 | 1 | 63.7423 | 16.4812 | 0 | 0 | 70.8248 | 16.4812 | 0.9
46 | cheetham_hill_PS | Cheetham Hill | 9.736 | 3.9446 | 1 | 9.736 | 3.9446 | 0 | 0 | 10.8177 | 3.9446 | 0.9
47 | clifton_junction_PS | Clifton Junction | 7.8465 | 2.2606 | 1 | 7.8465 | 2.2606 | 0 | 0 | 8.7184 | 2.2606 | 0.9
48 | prestwich_PS | Prestwich | 13.2708 | 4.0283 | 1 | 13.2708 | 4.0283 | 0 | 0 | 14.7453 | 4.0283 | 0.9
49 | swinton_PS | Swinton | 8.4053 | 2.7368 | 1 | 8.4053 | 2.7368 | 0 | 0 | 9.3392 | 2.7368 | 0.9
50 | the_height_PS | The Height | 9.5974 | 2.8652 | 1 | 9.5974 | 2.8652 | 0 | 0 | 10.6638 | 2.8652 | 0.9
51 | atherton_town_centre_PS | Atherton Town Centre | 22.1053 | 6.0181 | 1 | 22.1053 | 6.0181 | 0 | 0 | 24.5614 | 6.0181 | 0.9
52 | bedford_PS | Bedford | 15.4631 | 4.1626 | 1 | 15.4631 | 4.1626 | 0 | 0 | 17.1812 | 4.1626 | 0.9
53 | hindley_green_PS | Hindley Green | 16.042 | 5.4409 | 1 | 16.042 | 5.4409 | 0 | 0 | 17.8244 | 5.4409 | 0.9
54 | kirkhall_lane_PS | Kirkhall Lane | 9.2177 | 2.4897 | 1 | 9.2177 | 2.4897 | 0 | 0 | 10.2419 | 2.4897 | 0.9
55 | leigh_PS | Leigh | 5.4465 | 1.1629 | 1 | 5.4465 | 1.1629 | 0 | 0 | 6.0517 | 1.1629 | 0.9
56 | barbara_st_PS | Barbara St | 8.5353 | 3.3593 | 1 | 8.5353 | 3.3593 | 0 | 0 | 9.4837 | 3.3593 | 0.9
57 | bradshawgate_PS | Bradshawgate | 8.2833 | 2.4781 | 1 | 8.2833 | 2.4781 | 0 | 0 | 9.2037 | 2.4781 | 0.9
58 | cox_green_PS | Cox Green | 10.1281 | 2.2924 | 1 | 10.1281 | 2.2924 | 0 | 0 | 11.2534 | 2.2924 | 0.9
59 | harwood_PS | Harwood | 12.162 | 3.4044 | 1 | 12.162 | 3.4044 | 0 | 0 | 13.5133 | 3.4044 | 0.9
60 | musgrave_rd_PS | Musgrave Rd | 11.2243 | 2.2516 | 1 | 11.2243 | 2.2516 | 0 | 0 | 12.4714 | 2.2516 | 0.9
61 | spa_rd_PS | Spa Rd | 21.3925 | 6.1186 | 1 | 21.3925 | 6.1186 | 0 | 0 | 23.7694 | 6.1186 | 0.9
62 | union_rd_PS | Union Rd | 13.6472 | 3.6247 | 1 | 13.6472 | 3.6247 | 0 | 0 | 15.1636 | 3.6247 | 0.9
63 | wordsworth_st_PS | Wordsworth St | 11.3084 | 3.191 | 1 | 11.3084 | 3.191 | 0 | 0 | 12.5649 | 3.191 | 0.9
64 | bury_town_centre_PS | Bury Town Centre | 11.3247 | 2.7714 | 1 | 11.3247 | 2.7714 | 0 | 0 | 12.583 | 2.7714 | 0.9
65 | dumers_lane_PS | Dumers Lane | 9.3094 | 2.588 | 1 | 9.3094 | 2.588 | 0 | 0 | 10.3438 | 2.588 | 0.9
66 | heap_bridge_PS | Heap Bridge | 8.2066 | 2.5261 | 1 | 8.2066 | 2.5261 | 0 | 0 | 9.1184 | 2.5261 | 0.9
67 | holt_st_PS | Holt St | 10.8344 | 2.3947 | 1 | 10.8344 | 2.3947 | 0 | 0 | 12.0382 | 2.3947 | 0.9
68 | woolfold_PS | Woolfold | 9.774 | 2.0367 | 1 | 9.774 | 2.0367 | 0 | 0 | 10.86 | 2.0367 | 0.9

## gen
Bus ID | Bus Name | DFES Name | Gen Type | Pg_max | Pg_min | Qg_max | Qg_min | gen_cost_coef_0 | gen_cost_coef_1
10 | agecroft_BSP | Agecroft |  | 3.5626 | 0 | 0 | 0 | 0 | 0
11 | atherton_BSP | Atherton |  | 15.7163 | 0 | 0 | 0 | 0 | 0
12 | bolton_BSP | Bolton |  | 11.6357 | 0 | 0 | 0 | 0 | 0
13 | bury_BSP | Bury |  | 58.798 | 0 | 0 | 0 | 0 | 0
46 | cheetham_hill_PS | Cheetham Hill |  | 0.58936 | 0 | 0 | 0 | 0 | 0
47 | clifton_junction_PS | Clifton Junction |  | 1.8365 | 0 | 0 | 0 | 0 | 0
48 | prestwich_PS | Prestwich |  | 0.80345 | 0 | 0 | 0 | 0 | 0
49 | swinton_PS | Swinton |  | 0.62218 | 0 | 0 | 0 | 0 | 0
50 | the_height_PS | The Height |  | 1.5476 | 0 | 0 | 0 | 0 | 0
51 | atherton_town_centre_PS | Atherton Town Centre |  | 2.8933 | 0 | 0 | 0 | 0 | 0
52 | bedford_PS | Bedford |  | 5.3985 | 0 | 0 | 0 | 0 | 0
53 | hindley_green_PS | Hindley Green |  | 4.0841 | 0 | 0 | 0 | 0 | 0
54 | kirkhall_lane_PS | Kirkhall Lane |  | 2.2804 | 0 | 0 | 0 | 0 | 0
55 | leigh_PS | Leigh |  | 1.0599 | 0 | 0 | 0 | 0 | 0
56 | barbara_st_PS | Barbara St |  | 0.78898 | 0 | 0 | 0 | 0 | 0
57 | bradshawgate_PS | Bradshawgate |  | 1.0643 | 0 | 0 | 0 | 0 | 0
58 | cox_green_PS | Cox Green |  | 1.2779 | 0 | 0 | 0 | 0 | 0
59 | harwood_PS | Harwood |  | 1.3368 | 0 | 0 | 0 | 0 | 0
60 | musgrave_rd_PS | Musgrave Rd |  | 2.1108 | 0 | 0 | 0 | 0 | 0
61 | spa_rd_PS | Spa Rd |  | 2.7248 | 0 | 0 | 0 | 0 | 0
62 | union_rd_PS | Union Rd |  | 0.71057 | 0 | 0 | 0 | 0 | 0
63 | wordsworth_st_PS | Wordsworth St |  | 1.6215 | 0 | 0 | 0 | 0 | 0
64 | bury_town_centre_PS | Bury Town Centre |  | 0.63049 | 0 | 0 | 0 | 0 | 0
65 | dumers_lane_PS | Dumers Lane |  | 3.8239 | 0 | 0 | 0 | 0 | 0
66 | heap_bridge_PS | Heap Bridge |  | 13.0804 | 0 | 0 | 0 | 0 | 0
67 | holt_st_PS | Holt St |  | 1.1161 | 0 | 0 | 0 | 0 | 0
68 | woolfold_PS | Woolfold |  | 1.7887 | 0 | 0 | 0 | 0 | 0

## note
No | Modifications that are applied to the original data
1 | all impedance values (R and X) at both tn and dn levels are multiplied by a factor 0.1