## Disclaimer
Disclaimer
The information in this table should be read in conjunction with the explanatory notes in the main text.
The information contained in this statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes
in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval by Electricity North West, and payment of appropriate charges.
The information contained in this statement is the Copyright of Electricity North West, All Rights Reserved.

## HV Circuit Data - Published
HV INTERCONNECTOR DATA
From BSP or Substation Group | Node 1 | To BSP or Substation Group | Node 2 | HV Interconnector Name | Operating Voltage (kV) | Positive Sequence Resistance (%) | Positive Sequence Reactance (%) | Zero Sequence Resistance (%) | Zero Sequence Reactance (%) | Continuous (or Summer for OHL) | Cyclic (or Winter for OHL) | Circuit Length (km)
PRESTON EAST | BUSHELL ST | PRESTON EAST | CRAGGS ROW | BUSHELL ST - CRAGGS ROW | 6.6 | 0.14813 | 0.16853 | 0.44451 | 0.5056 | 460 | 520 | 0.158
ROSSENDALE | GRANE RD | ROSSENDALE | PRINNY HILL | GRANE RD - PRINNY HILL 1 | 6.6 | 8.5782 | 5.5049 | 25.6905 | 22.144 | 320 | 362 | 0.865
ROSSENDALE | GRANE RD | ROSSENDALE | PRINNY HILL | GRANE RD - PRINNY HILL 2 | 11 | 10.647 | 6.2244 | 31.941 | 24.752 | 355 | 401 | 0.91
STAINBURN | HDA1 | STAINBURN | HDA2 | HDA1 - HDA2 NO. 1 | 6.6 | 13.7246 | 8.13 | 43.3152 | 27.9044 | 270 | 360 | 1.156
CARLISLE | MORTON PARK | CARLISLE | PIRELLI | MORTON PARK - PIRELLI 1 | 11 | 11.97 | 9.6863 | 35.91 | 39.06 | 420 | 475 | 1.575
CARLISLE | MORTON PARK | CARLISLE | PIRELLI | MORTON PARK - PIRELLI 2 | 11 | 13.5483 | 10.4967 | 40.6305 | 42.3104 | 355 | 401 | 1.697
LEYLAND | MOSS SIDE (LEYLAND) | LEYLAND | SEVEN STARS | MOSS SIDE (LEYLAND) - SEVEN STARS 1 | 11 | 10.6274 | 9.2189 | 28.1689 | 14.5929 | 540 | 610 | 2
STAINBURN | HDA1 | STAINBURN | HDA2 | HDA1 - HDA2 NO. 3 (VIA BNFL) | 11 | 20.2776 | 15.4221 | 66.3544 | 50.5841 | 305 | 400 | 2.367
STAINBURN | HDA1 | STAINBURN | HDA2 | HDA1 - HDA2 NO. 2 (VIA WEST CUMBRIA COLLEGE) | 11 | 26.344 | 18.293 | 91.9107 | 43.7471 | 315 | 410 | 2.591
ULVERSTON | ASKAM | ULVERSTON | DALTON | ASKAM - DALTON 1 | 11 | 99.142 | 114.1377 | 177.1046 | 547.5436 | 250 | 283 | 4.668
PENRITH | SKELTON C | PENRITH | HUTTON | HUTTON END - SKELTON C | 11 | 34.1008 | 50.5321 | 272.5384 | 77.3009 | 270 | 305 | 5.129
ULVERSTON | ASKAM | ULVERSTON | DALTON | ASKAM - DALTON 2 | 11 | 67.3273 | 42.8777 | 272.787 | 24.1901 | 403 | 455 | 5.191
ULVERSTON | ASKAM | ULVERSTON | DALTON | ASKAM - DALTON (VIA NELSON ST) | 11 | 74.8328 | 30.3813 | 228.9457 | 111.7322 | 270 | 305 | 5.454
MOSS NOOK | ALDERLEY | MOSS NOOK | CHELFORD | ALDERLEY - CHELFORD | 11 | 90.5798 | 113.1707 | 212.6546 | 571.8981 | 355 | 401 | 6.7085

## 33kV Circuit Data - Published
33KV CIRCUIT DATA
From Substation Group | Node 1 | To Substation Group | Node 2 | Positive Sequence Resistance (%) | Positive Sequence Reactance (%) | Zero Sequence Resistance (%) | Zero Sequence Reactance (%) | Susceptance (%) | Continuous (or Summer for OHL) Rating (Amps) | Cyclic (or Winter for OHL) Rating (Amps) | Length (km)
Adswood | ADSWOOD | Adswood | BRAMHALL / CHEADLE HULME Tee | 1.6922 | 2.9932 | 11.6261 | 1.5212 | 0.29512 | 575 | 600 | 2.966
Adswood | ADSWOOD | Adswood | BRINKSWAY | 1.979 | 1.7219 | 7.8824 | 1.9162 | 0.2048 | 450 | 550 | 2.0897
Adswood | ADSWOOD | Adswood | BRINKSWAY / CHEADLE HEATH Tee | 1.0932 | 1.9271 | 1.8735 | 0.8833 | 0.1893 | 600 | 600 | 1.9078
Adswood | ADSWOOD | Adswood | CHEADLE HEATH | 1.8307 | 3.2289 | 3.138 | 1.4802 | 0.31721 | 400 | 510 | 3.197
Adswood | ADSWOOD | Adswood | CHEADLE HULME T12 | 2.9085 | 2.1707 | 6.3616 | 2.7063 | 0.3234 | 450 | 550 | 2.8235
Adswood | ADSWOOD | Adswood | WINIFRED RD T12 | 1.4699 | 0.9204 | 4.5541 | 1.0301 | 0.0816 | 275 | 311 | 1.025
Adswood | AGECROFT | Adswood | WINIFRED RD T11 | 1.5186 | 0.951 | 4.7051 | 1.0643 | 0.0843 | 275 | 311 | 1.059
Adswood | BRAMHALL / CHEADLE HULME Tee | Adswood | CHEADLE HULME T11 | 2.477 | 1.9377 | 4.5369 | 2.4756 | 0.32947 | 400 | 510 | 2.611
Adswood | BRINKSWAY / CHEADLE HEATH Tee | Adswood | BRINKSWAY | 0.18336 | 0.32323 | 0.31424 | 0.14816 | 0.031744 | 420 | 475 | 0.32
Adswood | BRINKSWAY / CHEADLE HEATH Tee | Adswood | CHEADLE HEATH | 2.2422 | 1.623 | 8.8725 | 3.2603 | 0.33852 | 450 | 550 | 1.954
Agecroft | AGECROFT | Agecoft | THE HEIGHT T11 | 3.0764 | 1.9488 | 9.6479 | 2.1971 | 0.17532 | 250 | 320 | 2.1812
Agecroft | AGECROFT | Agecroft | CHEETHAM HILL T11 | 5.4778 | 4.7663 | 21.8186 | 5.3042 | 0.56668 | 310 | 393 | 5.7843
Agecroft | AGECROFT | Agecroft | CHEETHAM HILL T12/FREDERICK RD TEE | 2.3397 | 2.0359 | 9.3194 | 2.2656 | 0.2421 | 310 | 393 | 2.4707
Agecroft | AGECROFT | Agecroft | CLIFTON JUNCTION Tee | 0.8996 | 0.7828 | 3.58 | 0.8712 | 0.0931 | 356 | 490 | 0.95
Agecroft | AGECROFT | Agecroft | PRESTWICH T12 | 1.9063 | 2.8081 | 10.7562 | 3.092 | 0.47408 | 435 | 550 | 3.1292
Agecroft | AGECROFT | Agecroft | SWINTON T12 | 3.2923 | 3.0852 | 15.1819 | 2.9861 | 0.30675 | 356 | 490 | 3.5167
Agecroft | AGECROFT | Agecroft | THE HEIGHT T12 | 3.0852 | 1.9548 | 9.6777 | 2.2041 | 0.17597 | 250 | 320 | 2.1882
Agecroft | CHEETHAM HILL T12 | Agecroft | CHEETHAM HILL T12/FREDERICK RD TEE | 3.1498 | 2.7407 | 12.5462 | 3.0501 | 0.326 | 310 | 393 | 3.3261
Agecroft | CLIFTON JUNCTION T11 | Agecroft | CLIFTON JUNCTION Tee | 1.7219 | 0.97325 | 4.7794 | 1.2394 | 0.064937 | 456 | 515 | 0.994
Agecroft | CLIFTON JUNCTION Tee | Agecroft | SWINTON T11 | 2.338 | 2.2712 | 11.5342 | 2.0471 | 0.20549 | 356 | 490 | 2.512
Agecroft | FREDERICK ROAD | Frederick Road | CHEETHAM HILL T12/FREDERICK RD TEE | 1.0193 | 0.8869 | 4.0598 | 0.987 | 0.1055 | 310 | 393 | 1.0763
Agecroft | PRESTWICH T11 | Agecoft | AGECROFT | 1.8604 | 2.7693 | 10.5462 | 3.0444 | 0.47439 | 435 | 550 | 3.1002
Agecroft | PRESTWICH T12 | Agecroft | MOSS LANE | 0.7774 | 1.4072 | 4.728 | 1.4639 | 0.1528 | 538 | 538 | 1.4879
Altrincham | ALTRINCHAM | Altrincham | MEDIPARK T11 | 3.1859 | 5.6162 | 5.4599 | 2.5743 | 0.55155 | 575 | 662 | 5.56
Altrincham | ALTRINCHAM | Altrincham | MEDIPARK T12 | 3.1859 | 5.6162 | 5.4599 | 2.5743 | 0.55155 | 575 | 662 | 5.56
Altrincham | ALTRINCHAM | Altrincham | BOWDON T11 | 3.1911 | 2.4198 | 5.4625 | 3.1245 | 0.40533 | 400 | 400 | 3.2604
Altrincham | ALTRINCHAM | Altrincham | BOWDON T12 | 3.275 | 2.4326 | 5.5638 | 3.1428 | 0.40117 | 400 | 400 | 3.2655
Altrincham | ALTRINCHAM | Altrincham | BROADHEATH T11 | 0.064811 | 0.079072 | 0.30923 | 0.04476 | 0.0050723 | 515 | 580 | 0.0706
Altrincham | ALTRINCHAM | Altrincham | BROADHEATH T13 | 0.069768 | 0.08512 | 0.33288 | 0.048184 | 0.0054602 | 515 | 580 | 0.076
Altrincham | ALTRINCHAM | Altrincham | GREEN LANE (Altrincham) T11 | 2.6697 | 1.9294 | 20.5852 | 1.2268 | 0.72679 | 427 | 535 | 3.44
Altrincham | ALTRINCHAM | Altrincham | GREEN LANE (Altrincham) T12 | 3.1579 | 3.7859 | 22.3135 | 2.1079 | 0.167 | 640 | 723 | 3.5237
Altrincham | GREEN LANE (Altrincham) T12 | Moss Nook | GATLEY | 4.4774 | 4.2912 | 27.5497 | 4.0052 | 1.2364 | 323 | 410 | 6.8875
Atherton | ATHERTON | Atherton | ATHERTON TOWN CENTRE T11 | 1.8363 | 1.6323 | 3.3428 | 2.1003 | 0.30271 | 476 | 640 | 2.2576
Atherton | ATHERTON | Atherton | ATHERTON TOWN CENTRE T12 | 1.4829 | 2.5257 | 1.483 | 2.1468 | 0.27691 | 670 | 750 | 2.5233
Atherton | ATHERTON | Atherton | BEDFORD T11 | 2.7986 | 2.4351 | 11.147 | 2.7099 | 0.2896 | 400 | 450 | 2.9552
Atherton | ATHERTON | Atherton | HINDLEY GREEN T13 | 6.1243 | 5.805 | 17.4996 | 17.0336 | 0.27111 | 245 | 315 | 4.27
Atherton | ATHERTON | Atherton | KIRKHALL LANE T11 | 1.8268 | 1.196 | 5.8677 | 1.3453 | 0.105 | 245 | 315 | 1.3246
Atherton | ATHERTON | Atherton | KIRKHALL LANE T12 | 1.3187 | 1.1877 | 5.4953 | 1.3615 | 0.11034 | 356 | 490 | 1.3198
Atherton | ATHERTON | Atherton | LEIGH T11 | 2.3896 | 2.8647 | 16.8842 | 1.595 | 0.1264 | 362 | 400 | 2.6663
Atherton | ATHERTON | Atherton | PPG T11 | 2.6542 | 2.816 | 6.7185 | 3.4247 | 0.46876 | 476 | 640 | 3.6521
Atherton | ATHERTON | Atherton | PPG T12 | 1.8914 | 3.4277 | 11.515 | 3.5654 | 0.3732 | 671 | 758 | 3.6233
Atherton | ATHERTON | Kearsley Local GSP | CUTACRE | 4.5531 | 8.0262 | 7.803 | 3.679 | 0.78824 | 590 | 667 | 7.946
Atherton | ATHERTON TOWN CENTRE T12 | Atherton | HINDLEY GREEN | 5.1599 | 8.8609 | 25.2854 | 30.7505 | 0.58482 | 356 | 410 | 5.705
Atherton | PPG | Atherton | HINDLEY GREEN T11 | 1.6297 | 1.8632 | 4.8832 | 2.1968 | 0.28261 | 476 | 640 | 2.3117
Atherton | WIGAN | Wigan | HINDLEY GREEN | 4.05 | 7.34 | 24.6606 | 7.64 | 0.799 | 645 | 645 | 7.7598
Barrow | BARROW (DEVONSHIRE RD) | Barrow | BOWATERS T11 | 2.2796 | 1.598 | 3.7931 | 2.0681 | 0.252 | 420 | 441 | 2.1216
Barrow | BARROW (DEVONSHIRE RD) | Barrow | BOWATERS T12 | 2.2777 | 1.5966 | 3.7899 | 2.0663 | 0.252 | 420 | 441 | 2.1198
Barrow | BARROW (DEVONSHIRE RD) | Barrow | BOWATERS T13 | 2.4373 | 2.2267 | 10.3485 | 2.5829 | 0.1834 | 360 | 410 | 2.3823
Barrow | BARROW (DEVONSHIRE RD) | Barrow | CHATSWORTH T11 | 0.9496 | 0.8263 | 3.7823 | 0.9195 | 0.0983 | 305 | 385 | 1.0027
Barrow | BARROW (DEVONSHIRE RD) | Barrow | CHATSWORTH T12 | 0.9439 | 0.8213 | 3.7598 | 0.914 | 0.0977 | 305 | 385 | 0.99677
Barrow | BARROW (DEVONSHIRE RD) | Sandgate | SANDGATE B | 2.272 | 2.0682 | 4.1792 | 2.6557 | 0.38838 | 490 | 515 | 2.8696
Barton | BARTON | Barton | BARTON DOCK RD T11 | 2.5223 | 2.1953 | 10.046 | 2.4436 | 0.25998 | 323 | 410 | 2.6589
Barton | BARTON | Barton | BARTON DOCK RD T12 | 3.0665 | 2.2529 | 11.7844 | 3.1422 | 0.23981 | 284 | 360 | 2.6561
Barton | BARTON | Barton | CHASSEN RD T11 | 6.1054 | 3.8517 | 18.9788 | 4.3185 | 0.34368 | 250 | 320 | 4.2974
Barton | BARTON | Barton | CHASSEN RD T12 | 4.1568 | 3.5669 | 18.1643 | 3.7537 | 0.37078 | 250 | 320 | 4.1104
Barton | BARTON | Barton | DUMPLINGTON T11 | 0.0551 | 0.066 | 0.389 | 0.0368 | 0.0029 | 750 | 750 | 0.061478
Barton | BARTON | Barton | DUMPLINGTON T13 | 0.0606 | 0.0727 | 0.428 | 0.0405 | 0.0032 | 750 | 750 | 0.067645
Barton | BARTON | Barton | LYONS RD T11 | 1.0887 | 1.9192 | 1.8658 | 0.8797 | 0.18848 | 500 | 600 | 1.9
Barton | BARTON | Barton | LYONS RD T12 | 1.099 | 1.9374 | 1.8835 | 0.88803 | 0.19027 | 323 | 410 | 1.918
Barton | BARTON | Barton | MEDIA CITY | 3.1515 | 5.5556 | 5.401 | 2.5465 | 0.5456 | 655 | 740 | 5.5
Barton | BARTON | Barton | MEDIA CITY | 3.1515 | 5.5556 | 5.401 | 2.5465 | 0.5456 | 655 | 740 | 5.5
Barton | BARTON | Barton | MONTON | 1.615 | 2.8481 | 2.8917 | 1.3098 | 0.28078 | 400 | 455 | 2.821
Barton | BARTON | Barton | MOUNT ST T11 | 0.92406 | 1.0528 | 1.9029 | 1.3204 | 0.21739 | 470 | 600 | 1.486
Barton | BARTON | Barton | MOUNT ST T12 | 0.93121 | 1.0557 | 1.9189 | 1.3306 | 0.21922 | 470 | 600 | 1.4977
Barton | BARTON | Barton | TRAFFORD PARK NORTH T11 | 2.1151 | 3.0775 | 8.2568 | 2.0212 | 0.35292 | 323 | 410 | 3.118
Barton | LYONS RD T12 | Barton | TRAFFORD PARK NORTH T12 | 1.0842 | 1.2182 | 6.5727 | 1.1909 | 0.17074 | 575 | 662 | 1.277
Barton | MONTON | Barton | MOUNT ST T11 | 2.4271 | 1.9934 | 4.3509 | 2.5689 | 0.3514 | 420 | 475 | 2.7197
Belfield | BELFIELD | Belfield | GALE | 2.1927 | 2.2662 | 9.6027 | 3.1184 | 0.408 | 495 | 605 | 3.048
Belfield | BELFIELD | Belfield | KINGSWAY T11 | 1.5318 | 3.1802 | 17.5491 | 1.625 | 0.353 | 660 | 726 | 3.33
Belfield | BELFIELD | Belfield | KINGSWAY T12 | 1.5318 | 3.1802 | 17.5491 | 1.625 | 0.353 | 660 | 726 | 3.33
Belfield | BELFIELD | Belfield | LITTLEBOROUGH T11 / MILNROW T11 | 0.34089 | 0.3925 | 2.5884 | 1.0839 | 0.1206 | 500 | 500 | 0.531
Belfield | BELFIELD | Belfield | WARDLEWORTH | 0.814 | 0.841 | 3.5656 | 1.16 | 0.152 | 495 | 600 | 1.1318
Belfield | CASTLETON | Castleton | MILNROW T12 | 5.8056 | 8.0704 | 30.0076 | 8.2396 | 0.6757 | 400 | 400 | 7.2
Belfield | LITTLEBOROUGH T11 | Belfield | LITTLEBOROUGH T11 / MILNROW T11 | 3.4107 | 5.9902 | 8.8642 | 18.1712 | 0.24188 | 500 | 500 | 3.253
Belfield | LITTLEBOROUGH T11 / MILNROW T11 | Belfield | MILNROW T11 | 1.6031 | 2.0925 | 2.4873 | 1.0719 | 0.16956 | 400 | 455 | 1.964
Belfield | ROCHDALE CENTRAL | Rochdale Central | WARDLEWORTH | 0.90064 | 1.0116 | 9.7358 | 0.59827 | 0.52637 | 480 | 600 | 1.9554
Belfield | WARDLEWORTH | Belfield | GALE | 1.1419 | 1.18 | 5.0007 | 1.62 | 0.213 | 495 | 600 | 1.5873
Bispham | BISPHAM | Bispham | CLEVELEYS T11 | 3.8066 | 3.364 | 17.743 | 3.445 | 0.3559 | 470 | 600 | 3.906
Bispham | BISPHAM | Bispham | NORBRECK | 1.75 | 1.5227 | 6.9706 | 1.6946 | 0.181 | 360 | 452 | 1.848
Bispham | BISPHAM | Bispham | NORBRECK T12 / POULTON Tee | 1.7289 | 1.9914 | 19.6857 | 1.1355 | 0.25378 | 364 | 409 | 1.902
Bispham | BISPHAM | Bispham | POULTON T11 | 4.1214 | 4.3293 | 18.3287 | 5.8936 | 0.78009 | 382 | 432 | 5.806
Bispham | BISPHAM | Bispham | WARBRECK | 2.4133 | 1.7907 | 9.288 | 2.4658 | 0.19205 | 324 | 407 | 2.1145
Bispham | BISPHAM | Bispham | WARBRECK | 2.4448 | 1.8168 | 9.4156 | 2.4968 | 0.19512 | 324 | 407 | 2.146
Bispham | BISPHAM | Blackpool | BLACKPOOL | 3.8188 | 4.0533 | 16.8698 | 5.5821 | 0.74816 | 495 | 620 | 5.481
Bispham | BISPHAM | Thornton | THORNTON PRIMARY A | 4.5482 | 4.6266 | 23.358 | 7.3966 | 0.82155 | 360 | 452 | 5.251
Bispham | CLEVELEYS T12 | Bispham | NORBRECK | 2.3842 | 2.1793 | 10.4789 | 2.2129 | 0.23085 | 360 | 452 | 2.5368
Bispham | NORBRECK T12 | Bispham | NORBRECK T12 / POULTON Tee | 0.062734 | 0.075852 | 0.0952 | 0.04011 | 0.005747 | 364 | 409 | 0.07
Bispham | NORBRECK T12 / POULTON Tee | Bispham | POULTON T12 | 10.0126 | 10.3359 | 51.5065 | 10.9599 | 1.2647 | 364 | 409 | 11.9
Blackburn | BLACKBURN | Blackburn | PRINGLE ST T12 | 4.9323 | 3.9216 | 19.3888 | 4.9943 | 0.42004 | 284 | 370 | 4.6075
Blackburn | BLACKBURN | Blackburn | RANDAL ST | 3.0374 | 2.6859 | 13.7033 | 2.8712 | 0.29053 | 279 | 350 | 3.1481
Blackburn | BLACKBURN | Blackburn | SAMLESBURY ENTERPRISE ZONE | 4.7355 | 9.8385 | 41.1705 | 4.6305 | 1.2642 | 612 | 709 | 10.5
Blackburn | BLACKBURN | Blackburn | SAMLESBURY ENTERPRISE ZONE | 4.7355 | 9.8385 | 41.1705 | 4.6305 | 1.2642 | 612 | 709 | 10.5
Blackburn | CLARENDON RD T11 / PRINGLE ST T11 Tee | Blackburn | CLARENDON RD T11 | 1.5718 | 1.6172 | 6.8655 | 2.2151 | 0.28861 | 360 | 452 | 2.17
Blackburn | CLARENDON RD T12 / RANDAL ST 2 Tee | Blackburn | CLARENDON RD T12 | 1.6264 | 2.3758 | 2.6132 | 1.1645 | 0.20925 | 490 | 554 | 2.28
Blackburn | CLARENDON RD T12 / RANDAL ST 2 Tee | Blackburn | RANDAL ST | 3.1478 | 3.6551 | 30.7736 | 2.0584 | 0.43371 | 279 | 350 | 3.471
Blackburn | PRINGLE ST T11 | Blackburn | CLARENDON RD T11 / PRINGLE ST T11 Tee | 4.4282 | 3.8701 | 17.7411 | 4.3238 | 0.44701 | 284 | 370 | 4.6451
Blackpool | BISPHAM | Bispham | CECIL STREET | 2.9897 | 2.6014 | 11.9 | 2.895 | 0.3094 | 360 | 414 | 3.157
Blackpool | BLACKPOOL | Blackpool | CECIL STREET | 3.1734 | 2.7612 | 12.64 | 3.0729 | 0.3284 | 324 | 405 | 3.351
Blackpool | BLACKPOOL | Blackpool | MARTON | 2.4246 | 4.394 | 14.7611 | 4.5705 | 0.47837 | 605 | 680 | 4.6448
Blackpool | BLACKPOOL | Blackpool | MARTON | 2.4333 | 4.4098 | 14.8142 | 4.5869 | 0.48013 | 605 | 680 | 4.6615
Blackpool | BLACKPOOL | Blackpool | PRESTON OLD RD T11 | 2.1238 | 2.5679 | 3.2229 | 1.3579 | 0.1946 | 470 | 600 | 2.3698
Blackpool | BLACKPOOL | Blackpool | PRESTON OLD RD T12 | 2.1332 | 2.5793 | 3.2372 | 1.3639 | 0.1954 | 490 | 554 | 2.3803
Blackpool | BLACKPOOL | Blackpool | SHANNON ST T14 | 0.0559 | 0.0486 | 0.223 | 0.0541 | 0.0058 | 324 | 407 | 0.059
Blackpool | MARTON | Blackpool | SQUIRES GATE | 1.4112 | 2.5574 | 8.5915 | 2.6602 | 0.2785 | 605 | 680 | 2.7034
Blackpool | PEEL | Peel | SQUIRES GATE | 4.4571 | 7.5311 | 19.7506 | 18.619 | 0.36384 | 370 | 420 | 5.129
Bloom Street | BLOOM ST | Bloom St | PICCADILLY T11 | 0.69814 | 0.84412 | 1.0594 | 0.44637 | 0.063956 | 455 | 519 | 0.779
Bloom Street | BLOOM ST | Bloom St | PICCADILLY T12 | 0.69545 | 0.84087 | 1.0554 | 0.44465 | 0.06371 | 455 | 519 | 0.776
Bloom Street | BLOOM STREET | Bloom Street | BRIDGEWATER T12 | 0.7544 | 0.9044 | 5.3302 | 0.5035 | 0.0399 | 400 | 400 | 0.84173
Bloom Street | BLOOM STREET | Bloom Street | DEANSGATE T11 | 1.0249 | 0.8917 | 4.0821 | 0.9924 | 0.1061 | 310 | 390 | 1.0822
Bloom Street | BLOOM STREET | Bloom Street | KNOTT MILL | 0.58375 | 0.51287 | 1.1411 | 0.66304 | 0.36189 | 520 | 600 | 1.3735
Bloom Street | BLOOM STREET | Bloom Street | KNOTT MILL | 0.31699 | 0.28176 | 0.57705 | 0.36255 | 0.20671 | 600 | 600 | 0.77439
Bloom Street | BLOOM STREET | Bloom Street | STUART STREET | 2.1334 | 4.5234 | 3.9128 | 2.1376 | 0.49305 | 631 | 753 | 4.647
Bloom Street | BLOOM STREET | Stuart Street | ARDWICK T11 / BLOOM STREET Tee | 0.63134 | 0.61767 | 2.9839 | 0.79165 | 0.080067 | 290 | 370 | 0.77047
Bloom Street | BLOOM STREET | Stuart Street | ARDWICK T12 / BLOOM STREET Tee | 0.62566 | 0.6119 | 2.9556 | 0.78396 | 0.07931 | 290 | 370 | 0.76321
Bloom Street | BRIDGEWATER T11 | Bloom Street | BLOOM STREET | 0.7381 | 0.8849 | 5.2156 | 0.4927 | 0.039 | 400 | 400 | 0.82363
Bloom Street | DEANSGATE T12 | Bloom Street | KNOTT MILL | 0.6258 | 0.5562 | 1.1392 | 0.7157 | 0.103 | 455 | 519 | 0.76936
Bloom Street | KNOTT MILL | Frederick Road | ST JOHN | 0.38243 | 0.81084 | 3.1821 | 0.38318 | 0.088381 | 645 | 745 | 0.833
Bloom Street | KNOTT MILL | Red Bank | BLACKFRIARS A | 1.774 | 1.5458 | 7.0793 | 1.7226 | 0.1821 | 320 | 400 | 1.8691
Bolton | BOLTON | Bolton | BARBARA ST T11 | 5.8382 | 4.3529 | 22.5789 | 5.9965 | 0.45531 | 235 | 298 | 5.0938
Bolton | BOLTON | Bolton | BRADSHAW | 1.7478 | 1.5536 | 3.1817 | 1.999 | 0.2877 | 400 | 484 | 2.1488
Bolton | BOLTON | Bolton | BRADSHAWGATE T11 | 3.5143 | 2.7158 | 15.8897 | 3.2621 | 0.24409 | 263 | 342 | 3
Bolton | BOLTON | Bolton | BRADSHAWGATE T13 | 2.0028 | 1.8625 | 4.122 | 2.4187 | 0.35409 | 476 | 640 | 2.5844
Bolton | BOLTON | Bolton | COX GREEN T12 | 5.9276 | 5.3171 | 41.2851 | 3.8308 | 0.27107 | 245 | 315 | 5.0222
Bolton | BOLTON | Bolton | HARWOOD T12 | 1.965 | 1.9935 | 4.8758 | 2.6216 | 0.39617 | 245 | 315 | 2.7841
Bolton | BOLTON | Bolton | MUSGRAVE RD T11 | 2.9672 | 2.5924 | 11.8827 | 2.8955 | 0.30015 | 356 | 403 | 3.114
Bolton | BOLTON | Bolton | PRINCE ST | 1.169 | 1.2847 | 6.1117 | 1.4086 | 0.19364 | 356 | 484 | 1.394
Bolton | BOLTON | Bolton | SPA RD T11 | 1.2504 | 2.2604 | 7.5955 | 2.3521 | 0.24551 | 356 | 473 | 2.391
Bolton | BOLTON | Bolton | SPA RD T12 | 1.3104 | 2.3718 | 7.9696 | 2.4676 | 0.2576 | 356 | 473 | 2.508
Bolton | BOLTON | Bolton | UNION RD T11 | 0.1412 | 0.129 | 0.5995 | 0.1496 | 0.0106 | 356 | 403 | 0.138
Bolton | BOLTON | Bolton | UNION RD T12 | 0.1494 | 0.1365 | 0.634 | 0.1583 | 0.0112 | 356 | 403 | 0.146
Bolton | BOLTON | Bolton | WORDSWORTH ST T11 | 1.3895 | 1.3873 | 3.4037 | 1.8259 | 0.27383 | 400 | 403 | 1.934
Bolton | BOLTON | Bolton | WORDSWORTH ST T12 | 2.7682 | 2.486 | 5.1859 | 3.2056 | 0.4632 | 400 | 403 | 3.441
Bolton | BRADSHAW | Bolton | HARWOOD T11 | 1.2582 | 1.12 | 2.29 | 1.439 | 0.2071 | 400 | 484 | 1.5468
Bolton | BRADSHAWGATE T13 | Bolton | BARBARA ST T12 | 1.6192 | 1.5928 | 3.8458 | 2.0894 | 0.31246 | 235 | 298 | 2.22
Bolton | COX GREEN T11 | Bolton | BRADSHAW | 4.2015 | 2.6311 | 13.0175 | 2.9445 | 0.233 | 245 | 315 | 2.9299
Bolton | MUSGRAVE RD T12 | Bolton | PRINCE ST | 1.5719 | 1.7397 | 7.8277 | 1.9288 | 0.25506 | 356 | 484 | 1.873
Bolton | SPA RD T13 | Bolton | PRINCE ST | 1.0309 | 1.041 | 5.5701 | 1.114 | 0.15368 | 356 | 484 | 1.123
Burnley | BURNLEY | Burnley | ATHLETIC STREET | 1.5147 | 3.3391 | 13.1611 | 1.7301 | 0.32244 | 378 | 474 | 3.366
Burnley | BURNLEY CENTRE | Burnley | ATHLETIC STREET | 0.6939 | 1.5297 | 6.0292 | 0.79259 | 0.14771 | 378 | 474 | 1.542
Burnley | BURNLEY CENTRE | Burnley | HEASANDFORD B | 1.6114 | 1.6784 | 7.2685 | 2.2321 | 0.28917 | 378 | 474 | 2.2183
Burnley | BURNLEY CENTRE | Huncoat | COG LANE T12 | 1.409 | 2.4838 | 9.6147 | 1.2639 | 0.24393 | 378 | 474 | 2.459
Burnley | BURNLEY NORTH T11 | Burnley | BURNLEY | 1.4591 | 1.3851 | 6.0921 | 1.7338 | 0.20984 | 378 | 474 | 1.777
Burnley | HEASANDFORD | Burnley | BURNLEY | 0.34681 | 0.73934 | 2.9108 | 0.38472 | 0.070271 | 515 | 605 | 0.741
Burnley | HEASANDFORD A | Burnley | BURNLEY | 0.5069 | 0.5239 | 2.2199 | 0.7209 | 0.0944 | 446 | 559 | 0.70463
Burnley | HEASANDFORD A | Huncoat | HUNCOAT | 14.115 | 22.2061 | 41.4045 | 62.3446 | 0.768 | 257 | 372 | 11.19
Bury | BURY | Bury | BURY TOWN CENTRE | 1.4674 | 1.553 | 2.8921 | 1.9703 | 0.31516 | 492 | 599 | 2.194
Bury | BURY | Bury | BURY TOWN CENTRE | 0.8308 | 0.9175 | 4.4989 | 1.1418 | 0.0892 | 400 | 440 | 1.051
Bury | BURY | Bury | DUMERS LANE | 3.0044 | 2.7329 | 5.5246 | 3.5095 | 0.51307 | 476 | 640 | 3.7915
Bury | BURY | Bury | HEAP BRIDGE | 2.2181 | 2.8693 | 4.3297 | 2.3869 | 0.40539 | 502 | 566 | 3.36
Bury | BURY | Bury | HOLT ST | 7.7114 | 13.0515 | 24.6697 | 52.0197 | 0.22097 | 356 | 480 | 6.364
Bury | BURY | Bury | WOOLFOLD | 1.4435 | 1.3882 | 2.7211 | 1.7744 | 0.26861 | 476 | 640 | 1.9395
Bury | BURY | Bury | WOOLFOLD | 1.6758 | 1.587 | 3.1371 | 2.031 | 0.30472 | 476 | 640 | 3.0897
Bury | CHAMBERHALL T11 | Bury | BURY | 0.0818 | 0.0748 | 0.348 | 0.0867 | 0.0062 | 334 | 367 | 0.08
Bury | CHAMBERHALL T12 | Bury | BURY | 0.09 | 0.0823 | 0.382 | 0.0954 | 0.0068 | 361 | 403 | 0.088
Bury | DUMERS LANE T11 | Bury | HEAP BRIDGE | 4.2219 | 6.7264 | 11.4296 | 24.7601 | 0.3722 | 463 | 500 | 4.374
Bury | HEAP BRIDGE | Castleton | HEADY HILL | 1.0595 | 1.1965 | 2.1549 | 1.5109 | 0.2499 | 476 | 640 | 1.702
Buxton | BUXTON | Buxton | ASHWOOD DALE T11 | 5.07 | 6.9571 | 11.2853 | 21.2872 | 0.10797 | 310 | 380 | 3.1172
Buxton | BUXTON | Buxton | ASHWOOD DALE T12 | 6.0426 | 7.5969 | 17.5285 | 19.4244 | 0.095585 | 310 | 380 | 3.458
Buxton | BUXTON | Buxton | BUXTON STOR | 0.48705 | 0.85859 | 0.8347 | 0.39355 | 0.08432 | 575 | 662 | 0.85
Buxton | BUXTON | Buxton | WATERSWALLOWS STOR | 0.48705 | 0.85859 | 0.8347 | 0.39355 | 0.08432 | 575 | 662 | 0.85
Buxton | BUXTON | New Mills | FERODO T11 | 17.2198 | 21.168 | 31.4231 | 63.4258 | 0.24104 | 370 | 370 | 7.619
Buxton | BUXTON STOR | Buxton | TUNSTEAD | 1.323 | 2.9165 | 11.4954 | 1.5112 | 0.28163 | 575 | 662 | 2.94
Buxton | WATERSWALLOWS STOR | Buxton | TUNSTEAD | 1.3185 | 2.9066 | 11.4563 | 1.506 | 0.28067 | 575 | 662 | 2.93
Buxton | WATERSWALLOWS T11 | Buxton | BUXTON | 0.0451 | 0.0392 | 0.18 | 0.0436 | 0.0047 | 367 | 400 | 0.047596
Buxton | WATERSWALLOWS T12 | Buxton | BUXTON | 0.0426 | 0.037 | 0.17 | 0.0412 | 0.0044 | 367 | 400 | 0.044954
Carlisle | ASPATRIA LINE SWITCH / SILLOTH T11 Tee | Carlisle | WESTNEWTON WINDFARM Tee | 0.63631 | 0.8201 | 0.93754 | 2.6319 | 0.000672 | 220 | 340 | 0.24
Carlisle | ASPATRIA LINE SWITCH / SILLOTH T11 Tee | Carlisle | WIGTON A | 22.156 | 21.0783 | 31.3649 | 110.007 | 0.057511 | 380 | 428 | 13.0706
Carlisle | ASPATRIA LINE SWITCH / SILLOTH T11 Tee | Stainburn | ASPATRIA LINE SWITCH | 0.62435 | 1.3495 | 1.2163 | 6.6373 | 0.0009135 | 220 | 340 | 0.435
Carlisle | CAPONTREE | Carlisle | WREAY SOLAR | 24.5341 | 52.5233 | 48.5467 | 249.2953 | 0.2441 | 571 | 678 | 18.3408
Carlisle | CAPONTREE / PIRELLI T12 Tee | Carlisle | PIRELLI T12 | 4.8973 | 6.2461 | 8.4009 | 19.3884 | 0.043198 | 400 | 400 | 2.044
Carlisle | CARLISLE | Carlisle | CAPONTREE / PIRELLI T12 Tee | 8.8501 | 20.3979 | 18.5248 | 97.7032 | 0.022789 | 400 | 400 | 7.051
Carlisle | CARLISLE | Carlisle | FUSEHILL | 1.791 | 3.9482 | 15.5618 | 2.0457 | 0.38126 | 670 | 744 | 3.98
Carlisle | CARLISLE | Carlisle | FUSEHILL | 2.748 | 3.0659 | 6.7857 | 2.8305 | 0.82328 | 425 | 480 | 3.854
Carlisle | CARLISLE | Carlisle | JAMES ST T11 | 2.3914 | 2.1374 | 9.909 | 2.469 | 0.25966 | 400 | 450 | 2.611
Carlisle | CARLISLE | Carlisle | JAMES ST T12 | 2.3894 | 2.1335 | 9.8883 | 2.4575 | 0.25902 | 400 | 450 | 2.6059
Carlisle | CARLISLE | Carlisle | MORTON PK T11 | 22.8174 | 22.8945 | 33.3953 | 109.5336 | 0.046237 | 190 | 295 | 7.226
Carlisle | CARLISLE | Carlisle | MORTON PK T12 | 23.2362 | 23.3089 | 33.7393 | 111.7145 | 0.045969 | 190 | 295 | 7.353
Carlisle | CARLISLE | Carlisle | PETTERILL BANK | 4.1006 | 4.9527 | 22.9715 | 6.7251 | 0.64323 | 425 | 480 | 6.1424
Carlisle | CARLISLE | Carlisle | SEBERGHAM T11 / WIGTON Tee | 35.6791 | 45.703 | 54.237 | 145.4449 | 0.10658 | 310 | 393 | 13.9139
Carlisle | CARLISLE | Carlisle | WESTLINTON | 14.0485 | 30.7523 | 33.2915 | 140.0699 | 0.17575 | 220 | 340 | 11.59
Carlisle | CARLISLE | Carlisle | WIGTON B | 49.1176 | 46.589 | 71.5152 | 240.4661 | 0.10531 | 300 | 361 | 15.0264
Carlisle | CARLISLE | Carlisle | WIGTON B | 33.9057 | 56.3537 | 58.1512 | 234.4085 | 0.091191 | 310 | 393 | 17.8238
Carlisle | CARLISLE | Carlisle | WILLOWHOLME T11 | 0.16595 | 0.25827 | 1.0039 | 0.14082 | 0.020144 | 455 | 519 | 0.242
Carlisle | CARLISLE | Carlisle | WILLOWHOLME T12 | 0.20105 | 0.32546 | 1.2675 | 0.17629 | 0.026179 | 455 | 519 | 0.308
Carlisle | FUSEHILL | Carlisle | PETTERILL BANK | 1.6647 | 1.8242 | 6.2825 | 2.3841 | 0.28056 | 425 | 480 | 2.3644
Carlisle | HALLBURN WINDFARM Tee | Spadeadam | EASTON T11 | 10.7582 | 13.6659 | 15.8171 | 42.1881 | 0.05143 | 237 | 296 | 4.36
Carlisle | HELLRIGG WINDFARM Tee | Carlisle | HELLRIGG WINDFARM | 0.57325 | 0.55796 | 0.81389 | 0.27881 | 0.036897 | 400 | 450 | 0.49
Carlisle | HELLRIGG WINDFARM Tee | Carlisle | SILLOTH T13 | 11.8822 | 15.1633 | 18.873 | 47.2384 | 0.044004 | 220 | 340 | 4.747
Carlisle | SEBERGHAM T11 / WIGTON Tee | Carlisle | WIGTON A | 12.4032 | 26.8078 | 24.2 | 131.854 | 0.0181 | 480 | 480 | 8.6416
Carlisle | SILLOTH T11 | Carlisle | WESTNEWTON WINDFARM Tee | 30.6384 | 39.488 | 45.1424 | 126.727 | 0.032357 | 220 | 340 | 11.556
Carlisle | SILLOTH T12 | Carlisle | WIGTON B | 40.8813 | 52.6132 | 60.6908 | 168.5162 | 0.061782 | 220 | 340 | 15.5429
Carlisle | WESTLINTON | Carlisle | CAPONTREE | 22.3792 | 48.3695 | 43.5968 | 237.904 | 0.0327 | 420 | 480 | 15.592
Carlisle | WESTLINTON | Carlisle | HALLBURN WINDFARM Tee | 10.4331 | 13.0827 | 15.3102 | 38.9431 | 0.084046 | 237 | 296 | 4.486
Carlisle | WESTNEWTON WINDFARM Tee | Carlisle | WESTNEWTON WINDFARM | 1.4039 | 1.3664 | 1.9932 | 0.6828 | 0.09036 | 400 | 400 | 1.2
Carlisle | WIGTON A | Carlisle | CARLISLE | 49.2168 | 46.6838 | 71.7402 | 240.9757 | 0.10593 | 300 | 361 | 15.0599
Carlisle | WIGTON A | Carlisle | HELLRIGG WINDFARM Tee | 32.6852 | 42.126 | 48.1581 | 135.193 | 0.034518 | 220 | 340 | 12.328
Carlisle | WREAY SOLAR | Carlisle | CAPONTREE / PIRELLI T12 Tee | 7.9106 | 17.5369 | 15.8511 | 76.8367 | 0.18039 | 571 | 678 | 6.0897
Carrington | ALTRINCHAM | Altrincham | BROADHEATH T12 | 0.065362 | 0.079744 | 0.31186 | 0.045141 | 0.0051154 | 515 | 580 | 0.0712
Carrington | CARRINGTON | Carrington | AIR PRODUCTS T12 | 0.1888 | 0.1643 | 0.7521 | 0.1828 | 0.0195 | 400 | 400 | 0.19939
Carrington | CARRINGTON | Carrington | CARRINGTON STOR Tee | 1.2508 | 1.3728 | 10.452 | 0.75667 | 0.15226 | 220 | 365 | 1.2827
Carrington | CARRINGTON | Carrington | MARTENS RD STOR Tee | 1.2625 | 2.6768 | 2.3155 | 1.265 | 0.29178 | 645 | 746 | 2.75
Carrington | CARRINGTON | Carrington | NWGB PARTINGTON T11 | 1.2334 | 1.07 | 4.9129 | 1.1944 | 0.128 | 220 | 365 | 1.3025
Carrington | CARRINGTON STOR Tee | Carrington | NWGB PARTINGTON T12 | 0.68928 | 0.72606 | 4.0588 | 0.3879 | 0.069838 | 220 | 365 | 0.665
Carrington | MARTENS RD STOR Tee | Carrington | IRLAM T12 | 0.80342 | 1.7035 | 1.4735 | 0.805 | 0.18567 | 645 | 746 | 1.75
Carrington BSP | Carrington BSP | Carrington | IRLAM T11 | 2.583 | 3.3319 | 25.3739 | 1.8704 | 0.36865 | 420 | 475 | 3.164
Castleton | CASTLETON | Belfield | BELFIELD | 0.33176 | 0.38235 | 2.5235 | 1.0538 | 0.11773 | 422 | 565 | 0.517
Castleton | CASTLETON | Belfield | LITTLEBOROUGH T12 | 3.4107 | 5.9902 | 8.8642 | 18.1712 | 0.24188 | 500 | 500 | 3.253
Castleton | CASTLETON | Castleton | HEYWOOD T11 | 2.9113 | 2.7687 | 8.3215 | 3.5234 | 0.43122 | 356 | 403 | 3.6091
Castleton | CASTLETON | Castleton | HEYWOOD T12 | 2.4639 | 4.3434 | 16.813 | 2.2102 | 0.42656 | 356 | 403 | 4.3
Castleton | CASTLETON | Castleton | WOODBINE ST | 2.697 | 3.3847 | 4.1366 | 1.7621 | 0.26528 | 456 | 515 | 3.15
Castleton | CASTLETON | Castleton | WOODBINE ST | 2.654 | 3.8742 | 8.7844 | 4.7141 | 0.50317 | 381 | 476 | 3.7179
Castleton | HEADY HILL | Castleton | CASTLETON | 4.6201 | 4.1066 | 8.4104 | 5.2841 | 0.7606 | 476 | 640 | 5.68
Chadderton | CHADDERTON | Chadderton | HOLLINWOOD | 1.5831 | 1.6084 | 7.119 | 1.816 | 0.18037 | 380 | 450 | 1.8809
Chadderton | CHADDERTON | Chadderton | HOLLINWOOD | 1.5609 | 1.5919 | 7.0276 | 1.7958 | 0.17852 | 380 | 450 | 1.8602
Chadderton | CHADDERTON | Chadderton | LANGLEY | 2.7315 | 4.8152 | 4.6812 | 2.2071 | 0.47289 | 530 | 600 | 4.767
Chadderton | CHADDERTON | Chadderton | MIDDLETON JUNCTION T11 | 2.3538 | 3.4548 | 15.2394 | 7.9108 | 0.17425 | 380 | 450 | 1.976
Chadderton | CHADDERTON | Chadderton | MIDDLETON JUNCTION T12 | 2.3343 | 3.4398 | 14.9049 | 7.9016 | 0.17076 | 380 | 450 | 1.961
Chadderton | CHADDERTON | Chadderton | NEW MOSTON | 1.4299 | 2.5516 | 2.4609 | 1.1722 | 0.25258 | 575 | 662 | 2.533
Chadderton | CHADDERTON | Chadderton | NEW MOSTON | 1.4321 | 2.5556 | 2.4647 | 1.1741 | 0.25298 | 475 | 600 | 2.537
Chadderton | CHADDERTON | Greenhill | WILLOWBANK | 4.3046 | 3.7455 | 17.1457 | 4.1682 | 0.4455 | 350 | 410 | 4.5455
Chadderton | CHADDERTON | Royton | STOCK LANE | 2.2692 | 2.7713 | 23.3439 | 1.5294 | 0.33988 | 410 | 500 | 2.6628
Chadderton | FAILSWORTH | Chadderton | HOLLINWOOD | 1.2521 | 1.4341 | 6.979 | 2.0045 | 0.19351 | 475 | 600 | 1.8077
Chadderton | FAILSWORTH | Stuart Street | NEWTON HEATH A | 3.4516 | 2.4765 | 12.7803 | 2.8075 | 0.28276 | 475 | 600 | 2.465
Chadderton | LANGLEY | Chadderton | TOWNLEY ST | 1.1561 | 1.1948 | 5.0629 | 1.6441 | 0.2152 | 530 | 600 | 1.607
Chadderton | NEW MOSTON | Chadderton | FAILSWORTH | 1.7541 | 1.9273 | 9.74 | 2.7569 | 0.2685 | 425 | 540 | 2.4615
Chadderton | NEWTON HEATH B | Red Bank | Harpurhey | 1.7014 | 3.7508 | 14.7837 | 1.9434 | 0.36219 | 600 | 600 | 3.781
Chadderton | TOWNLEY ST | Chadderton | CHADDERTON | 4.3062 | 6.8141 | 9.496 | 21.5981 | 0.099192 | 380 | 450 | 2.867
Chadderton | TOWNLEY ST | Chadderton | CHADDERTON | 4.3818 | 6.9617 | 9.5957 | 22.1363 | 0.097768 | 380 | 450 | 2.902
Droylsden | DENTON EAST | Droylsden | DENTON WEST B | 1.8852 | 3.3232 | 12.8639 | 1.6911 | 0.32637 | 470 | 600 | 3.29
Droylsden | DENTON WEST A | Longsight | LONGSIGHT | 8.1246 | 5.1134 | 25.2948 | 5.7359 | 0.45503 | 250 | 320 | 5.6993
Droylsden | DROYLSDEN | Bloom Street | STUART STREET | 2.9168 | 4.6281 | 13.1315 | 2.2297 | 0.48282 | 385 | 400 | 4.548
Droylsden | DROYLSDEN | Droylsden | DENTON EAST | 3.211 | 4.174 | 6.0408 | 3.7223 | 0.64378 | 470 | 600 | 5.076
Droylsden | DROYLSDEN | Droylsden | DENTON WEST A | 7.102 | 5.2711 | 50.905 | 3.2652 | 0.49032 | 310 | 390 | 4.737
Droylsden | DROYLSDEN | Droylsden | DENTON WEST B | 7.6409 | 4.877 | 19.6621 | 5.3762 | 0.32797 | 230 | 290 | 4.8204
Droylsden | DROYLSDEN | Droylsden | DROYLSDEN EAST T11 | 0.4396 | 0.3825 | 1.7508 | 0.4256 | 0.0455 | 300 | 380 | 0.46416
Droylsden | DROYLSDEN | Droylsden | DROYLSDEN EAST T12 | 0.4819 | 0.4403 | 2.0462 | 0.5107 | 0.0363 | 300 | 380 | 0.47103
Droylsden | DROYLSDEN | Droylsden | OPENSHAW T11 | 2.8861 | 4.4201 | 15.5144 | 2.1668 | 0.47088 | 310 | 390 | 4.332
Droylsden | DROYLSDEN | Droylsden | OPENSHAW T12 | 2.6613 | 3.7181 | 4.6691 | 2.5061 | 0.44818 | 270 | 345 | 4.059
Droylsden | DROYLSDEN | Droylsden | SNIPE T11 | 2.2206 | 2.6621 | 15.6902 | 1.4822 | 0.11745 | 300 | 380 | 2.4777
Droylsden | DROYLSDEN | Droylsden | SNIPE T12 | 2.1145 | 2.5349 | 14.9404 | 1.4114 | 0.1118 | 300 | 380 | 2.3594
Egremont | BECKERMET MINE T11 | Egremont | BECKERMET MINE Tee | 0.086931 | 0.10511 | 0.13192 | 0.055581 | 0.0079637 | 600 | 600 | 0.097
Egremont | BECKERMET MINE Tee | Egremont | CARLETON T11 Tee | 10.0381 | 14.8237 | 15.9967 | 56.6898 | 0.10028 | 285 | 354 | 5.24
Egremont | CARLETON T11 Tee | Egremont | CARLETON T11 | 15.2527 | 21.313 | 23.5495 | 95.176 | 0.018168 | 380 | 400 | 6.1032
Egremont | EGREMONT | Egremont | BECKERMET MINE Tee | 7.4504 | 15.5333 | 14.4538 | 73.0035 | 0.00992 | 230 | 265 | 5.227
Egremont | EGREMONT | Egremont | HENSINGHAM | 7.7066 | 16.3537 | 24.1938 | 75.0048 | 0.21557 | 425 | 480 | 6.1481
Egremont | EGREMONT | Egremont | MIDWAY T11 | 23.6071 | 39.3369 | 40.0904 | 171.7376 | 0.0854 | 230 | 265 | 12.82
Egremont | EGREMONT | Egremont | MIDWAY T12 | 36.5848 | 47.1519 | 53.9036 | 151.322 | 0.0386 | 230 | 340 | 13.7988
Egremont | EGREMONT | Egremont | SLIPWAY | 6.5215 | 5.7958 | 6.9371 | 4.9103 | 2.1254 | 425 | 480 | 8.118
Egremont | SLIPWAY | Egremont | HENSINGHAM | 1.2042 | 1.1275 | 1.5737 | 0.94403 | 0.41766 | 425 | 481 | 1.572
Frederick Road | CHAPEL WHARF T12 | Red Bank | STRANGEWAYS T12 | 0.8055 | 1.7757 | 6.9989 | 0.92006 | 0.17147 | 571 | 668 | 1.79
Frederick Road | FREDERICK ROAD | Frederick Road | BLACKFRIARS B | 1.035 | 2.2816 | 8.993 | 1.1822 | 0.22032 | 600 | 600 | 2.3
Frederick Road | FREDERICK ROAD | Frederick Road | BLACKFRIARS T11 | 2.0487 | 1.7832 | 8.1639 | 1.9851 | 0.21209 | 290 | 370 | 2.1622
Frederick Road | FREDERICK ROAD | Frederick Road | CHAPEL WHARF T11 | 1.0809 | 2.3789 | 9.0772 | 1.2282 | 0.23094 | 600 | 600 | 2.4
Frederick Road | FREDERICK ROAD | Frederick Road | CHAPEL WHARF T12 | 1.0809 | 2.3789 | 9.0772 | 1.2282 | 0.23094 | 600 | 600 | 2.4
Frederick Road | FREDERICK ROAD | Frederick Road | FREDERICK ROAD T11 | 0.0575 | 0.0631 | 0.319 | 0.0903 | 0.0088 | 402 | 510 | 0.080634
Frederick Road | FREDERICK ROAD | Frederick Road | FREDERICK ROAD T12 | 0.056 | 0.0616 | 0.311 | 0.0881 | 0.0086 | 340 | 383 | 0.078626
Frederick Road | FREDERICK ROAD | Frederick Road | PENDLETON T11 | 0.77195 | 0.70647 | 1.4233 | 0.90675 | 0.13309 | 400 | 400 | 0.9809
Frederick Road | FREDERICK ROAD | Frederick Road | PENDLETON T12 | 0.7865 | 0.7193 | 1.4497 | 0.92326 | 0.13541 | 400 | 400 | 0.99861
Frederick Road | FREDERICK ROAD | Frederick Road | ROBERT HALL ST T11 | 1.9274 | 1.7581 | 8.1642 | 2.0367 | 0.14674 | 382 | 415 | 1.8889
Frederick Road | FREDERICK ROAD | Frederick Road | ROBERT HALL ST T12 / SALFORD QUAYS Tee | 0.7639 | 1.3844 | 4.6507 | 1.44 | 0.1507 | 600 | 600 | 1.4634
Frederick Road | FREDERICK ROAD | Frederick Road | SALFORD QUAYS T11 | 2.8511 | 2.9494 | 15.6072 | 2.4606 | 0.20182 | 420 | 475 | 3.0113
Frederick Road | FREDERICK ROAD | Frederick Road | ST JOHN | 1.1925 | 2.6288 | 10.3615 | 1.3621 | 0.25385 | 524 | 594 | 2.65
Frederick Road | FREDERICK ROAD | Frederick Road | TRINITY T11 | 0.8874 | 1.6082 | 5.4026 | 1.6728 | 0.1751 | 290 | 370 | 1.7
Frederick Road | FREDERICK ROAD | Frederick Road | TRINITY T12 | 1.55 | 1.8582 | 10.9523 | 1.0346 | 0.082 | 290 | 370 | 1.7296
Frederick Road | FREDERICK ROAD | Frederick Road | TRINITY T13 | 0.738 | 1.6269 | 6.4124 | 0.84296 | 0.1571 | 575 | 662 | 1.64
Frederick Road | FREDERICK ROAD | Frederick Road | WEASTE T12 | 4.0759 | 2.8917 | 6.8108 | 3.7412 | 0.46059 | 402 | 510 | 3.8483
Frederick Road | ROBERT HALL ST T12 | Frederick Road | ROBERT HALL ST T12 / SALFORD QUAYS Tee | 0.29205 | 0.25545 | 1.1711 | 0.2856 | 0.02931 | 400 | 400 | 0.30598
Frederick Road | ROBERT HALL ST T12 / SALFORD QUAYS Tee | Frederick Road | SALFORD QUAYS T12 | 1.3306 | 1.5952 | 9.4017 | 0.8881 | 0.0704 | 530 | 600 | 1.4847
Frederick Road | ST JOHN | Frederick Road | ST JOHN | 1.1925 | 2.6288 | 10.3615 | 1.3621 | 0.25385 | 524 | 594 | 2.65
Frederick Road | ST JOHN | Frederick Road | WEASTE T11 | 4.1229 | 2.9357 | 6.8983 | 3.7978 | 0.469 | 402 | 510 | 3.9097
Frederick Road | TRINITY T13 | Bloom Street | KNOTT MILL | 0.57388 | 1.2167 | 4.775 | 0.575 | 0.13262 | 645 | 745 | 1.25
Golborne | ASHTON / GOLBORNE / LANDGATE Line Switch Tee | Golborne | ASHTON (Golborne) T11 | 1.5346 | 3.1326 | 4.4922 | 14.1252 | 0.031132 | 367 | 367 | 1.192
Golborne | GOLBORNE | Golborne | Ashton/Golborne/Landgate Line Switch Tee | 7.4702 | 14.8553 | 26.4231 | 66.336 | 0.1988 | 331 | 367 | 5.764
Golborne | GOLBORNE | Golborne | CULCHETH T12 | 12.4054 | 13.963 | 36.0121 | 46.2298 | 0.57242 | 315 | 355 | 9.3219
Golborne | GOLBORNE | Golborne | HAYDOCK T11 | 1.8486 | 4.0751 | 16.0623 | 2.1115 | 0.39352 | 605 | 680 | 4.108
Golborne | GOLBORNE | Golborne | LODGE LANE SOUTH | 3.5632 | 5.572 | 7.4304 | 21.6678 | 0.32019 | 400 | 440 | 3.591
Golborne | GOLBORNE | Golborne | RISLEY T11 | 12.4629 | 17.5284 | 33.6808 | 59.3934 | 0.60023 | 280 | 380 | 10.0344
Golborne | HAYDOCK | Golborne | ASHTON (Golborne) T12 | 3.1275 | 4.5815 | 21.9332 | 7.9522 | 0.45176 | 350 | 385 | 3.85
Golborne | HAYDOCK | Golborne | GOLBORNE | 4.992 | 7.5034 | 15.1417 | 20.5947 | 0.33625 | 350 | 380 | 4.0892
Golborne | HAYDOCK | Golborne | HAYDOCK T11 | 0.066269 | 0.14609 | 0.57581 | 0.075694 | 0.014107 | 605 | 680 | 0.14727
Golborne | HAYDOCK | Golborne | HAYDOCK T12 | 0.084231 | 0.14849 | 0.14435 | 0.068061 | 0.014582 | 605 | 680 | 0.147
Golborne | HAYDOCK | Golborne | NEWTON LE WILLOWS | 2.9073 | 4.6642 | 5.3452 | 20.1236 | 0.12519 | 400 | 440 | 2.285
Golborne | HAYDOCK T12 | Golborne | GOLBORNE | 2.229 | 3.9293 | 3.82 | 1.8011 | 0.38589 | 605 | 680 | 3.89
Golborne | NEWTON LE WILLOWS | Golborne | LODGE LANE SOUTH | 1.1589 | 1.0762 | 2.1041 | 1.3078 | 0.19123 | 500 | 545 | 1.452
Golborne | ORRELL | Orrell | ASHTON (Golborne) T12 | 7.6576 | 11.4161 | 58.3185 | 5.8848 | 1.2359 | 575 | 662 | 11.165
Golborne | WIGAN | Wigan | ASHTON / GOLBORNE / LANDGATE Line Switch Tee | 4.6741 | 7.4 | 30.1997 | 20.6262 | 0.44077 | 356 | 400 | 4.804
Greenhill | GREENHILL | Greenhill | BELGRAVE T11 | 1.9593 | 1.7049 | 7.8043 | 1.8973 | 0.203 | 310 | 390 | 2.069
Greenhill | GREENHILL | Greenhill | BELGRAVE T12 | 1.966 | 1.7106 | 7.8307 | 1.9037 | 0.2034 | 310 | 390 | 2.076
Greenhill | GREENHILL | Greenhill | ST MARYS A | 2.1163 | 1.6836 | 8.1493 | 2.3389 | 0.2618 | 400 | 440 | 2.204
Greenhill | GREENHILL | Greenhill | ST MARYS B | 1.2665 | 1.0076 | 4.877 | 1.3997 | 0.1567 | 530 | 645 | 1.319
Greenhill | GREENHILL | Greenhill | WATERHEAD T11 | 1.9586 | 2.9813 | 11.7256 | 1.6317 | 0.23083 | 400 | 490 | 2.78
Greenhill | GREENHILL | Greenhill | WATERHEAD T12 | 1.9646 | 2.9926 | 11.824 | 1.6377 | 0.23275 | 400 | 490 | 2.792
Greenhill | GREENHILL | Greenhill | WERNETH T11 | 2.7965 | 2.4333 | 11.1 | 2.7079 | 0.2894 | 400 | 490 | 2.953
Greenhill | GREENHILL | Greenhill | WERNETH T12 | 2.7482 | 2.3913 | 10.9463 | 2.6611 | 0.2844 | 400 | 490 | 2.902
Greenhill | ROYTON | Royton | WILLOWBANK | 1.4223 | 1.4699 | 6.2285 | 2.0227 | 0.2647 | 530 | 645 | 1.977
Greenhill | ST MARYS A | Greenhill | WILLOWBANK | 0.7449 | 1.3131 | 1.2766 | 0.6019 | 0.12896 | 600 | 600 | 1.3
Greenhill | WILLOWBANK | Greenhill | ST MARYS B | 1.22 | 0.974 | 4.7143 | 1.35 | 0.151 | 450 | 550 | 1.275
Hazel Grove | ADSWOOD | Adswood | OFFERTON | 1.6408 | 2.8924 | 2.8119 | 1.3258 | 0.28405 | 575 | 600 | 2.8634
Hazel Grove | ADSWOOD | Adswood | OFFERTON | 1.6283 | 2.8703 | 2.7905 | 1.3157 | 0.28189 | 575 | 600 | 2.8416
Hazel Grove | BRAMHALL | Hazel Grove | NORBURY | 3.3737 | 2.684 | 12.9914 | 3.73 | 0.417 | 450 | 550 | 3.5136
Hazel Grove | DISLEY T12 | Hazel Grove | HAWK GREEN | 4.2399 | 8.9769 | 9.253 | 43.1368 | 0.0162 | 373 | 464 | 3.0354
Hazel Grove | HAWK GREEN | Hazel Grove | MARPLE T11 | 2.9605 | 1.8539 | 9.1726 | 2.0748 | 0.1643 | 360 | 450 | 2.0645
Hazel Grove | HAZEL GROVE | Hazel Grove | BRAMHALL | 2.3994 | 1.9089 | 9.2396 | 2.6518 | 0.2969 | 450 | 550 | 2.4989
Hazel Grove | HAZEL GROVE | Hazel Grove | GREEN LANE T11-Hazel Grove | 0.4691 | 0.4082 | 1.8686 | 0.4543 | 0.0485 | 321 | 353 | 0.49538
Hazel Grove | HAZEL GROVE | Hazel Grove | GREEN LANE T12-Hazel Grove | 0.5902 | 0.5136 | 2.3509 | 0.5715 | 0.0611 | 321 | 353 | 0.62324
Hazel Grove | HAZEL GROVE | Hazel Grove | HAWK GREEN | 4.3319 | 7.6364 | 29.5596 | 3.8858 | 0.74995 | 500 | 600 | 7.56
Hazel Grove | HAZEL GROVE | Hazel Grove | HAZEL GROVE | 4.3319 | 7.6364 | 29.5596 | 3.8858 | 0.74995 | 500 | 600 | 7.56
Hazel Grove | HAZEL GROVE | Hazel Grove | NORBURY | 1.6924 | 1.7491 | 7.4116 | 2.4069 | 0.315 | 495 | 600 | 2.3525
Hazel Grove | HAZEL GROVE | Hazel Grove | NORBURY | 1.684 | 1.7404 | 7.3749 | 2.3949 | 0.313 | 495 | 600 | 2.3409
Hazel Grove | HAZEL GROVE | Hazel Grove | OFFERTON | 1.9664 | 3.4663 | 3.3699 | 1.5889 | 0.34042 | 575 | 600 | 3.4317
Hazel Grove | HAZEL GROVE | Hazel Grove | OFFERTON | 1.9105 | 3.3679 | 3.2742 | 1.5437 | 0.33076 | 575 | 600 | 3.3342
Hazel Grove | NORBURY | Hazel Grove | POYNTON T11 | 1.3703 | 2.4156 | 2.3484 | 1.1072 | 0.2372 | 310 | 390 | 2.3914
Hazel Grove | POYNTON T12 | Hazel Grove | NORBURY | 1.3759 | 2.4255 | 2.3581 | 1.1118 | 0.23821 | 310 | 390 | 2.4013
Hazel Grove | VERNON PARK | Vernon Park | OFFERTON | 4.0252 | 2.5207 | 12.4715 | 2.821 | 0.2234 | 310 | 380 | 2.807
Hazel Grove | VERNON PARK | Vernon Park | OFFERTON | 3.932 | 2.4623 | 12.1827 | 2.7557 | 0.2183 | 310 | 380 | 2.742
Heyrod | ASHTON UNDER LYNE A | Heyrod | ASHTON UNDER LYNE T11 | 0.1754 | 0.1098 | 0.543 | 0.1229 | 0.0097 | 360 | 400 | 0.12231
Heyrod | ASHTON UNDER LYNE B | Heyrod | ASHTON UNDER LYNE T12 | 0.1806 | 0.1131 | 0.5595 | 0.1266 | 0.01 | 373 | 464 | 0.12592
Heyrod | ASHTON UNDER LYNE C | Heyrod | ASHTON UNDER LYNE T13 | 0.1725 | 0.108 | 0.534 | 0.1209 | 0.0096 | 495 | 620 | 0.12029
Heyrod | GLOSSOP / NEW MILLS TEE | New Mills | NEW MILLS | 18.1235 | 34.5915 | 32.8279 | 154.856 | 0.038952 | 350 | 350 | 10.82
Heyrod | GLOSSOP T12 | Heyrod | GLOSSOP / NEW MILLS TEE | 2.5146 | 4.5219 | 7.4521 | 8.534 | 0.2813 | 470 | 530 | 3.46
Heyrod | HATTERSLEY / HEYROD TEE | Heyrod | GLOSSOP / NEW MILLS TEE | 3.7634 | 8.134 | 7.3314 | 40.0067 | 0.0055062 | 530 | 350 | 2.622
Heyrod | HATTERSLEY / HEYROD TEE | Hyde | HATTERSLEY | 0.89007 | 1.8841 | 1.6314 | 0.89014 | 0.2052 | 530 | 530 | 1.935
Heyrod | HEYROD | Heyrod | ASHTON UNDER LYNE A | 3.9957 | 7.8608 | 15.041 | 27.2831 | 0.73103 | 400 | 530 | 4.84
Heyrod | HEYROD | Heyrod | ASHTON UNDER LYNE B | 5.1583 | 8.4344 | 11.9322 | 27.2631 | 0.41869 | 400 | 530 | 5.213
Heyrod | HEYROD | Heyrod | GREENFIELD T11 | 5.3817 | 7.3959 | 30.6067 | 5.0523 | 0.70481 | 400 | 490 | 7.176
Heyrod | HEYROD | Heyrod | GREENFIELD T12 | 5.4277 | 7.4814 | 35.182 | 4.7148 | 0.70081 | 400 | 490 | 7.17
Heyrod | HEYROD | Heyrod | HATTERSLEY / HEYROD TEE | 5.8617 | 10.7538 | 20.0788 | 47.7091 | 0.49744 | 530 | 530 | 5.342
Heyrod | HEYROD | Heyrod | HEYROD T11 | 0.041275 | 0.054646 | 0.25572 | 0.067736 | 0.006032 | 515 | 580 | 0.065
Heyrod | HEYROD | Heyrod | HEYROD T12 | 0.0388 | 0.0513 | 0.24 | 0.0636 | 0.0057 | 515 | 580 | 0.061053
Heyrod | HEYROD | Heyrod | HURST | 4.2055 | 6.9179 | 13.0166 | 22.3979 | 0.40308 | 400 | 530 | 3.543
Heyrod | HEYROD | Heyrod | MOSSLEY T11 | 1.5582 | 1.6104 | 6.824 | 2.216 | 0.29 | 593 | 678 | 2.166
Heyrod | HEYROD | Heyrod | MOSSLEY T12 | 1.6028 | 1.6565 | 7.0193 | 2.2795 | 0.2983 | 593 | 678 | 2.228
Heyrod | HEYROD | Heyrod | TAME VALLEY T11 | 2.5818 | 3.687 | 14.6535 | 1.86 | 0.3875 | 400 | 400 | 3.576
Heyrod | HEYROD | Heyrod | TAME VALLEY T12 | 2.5571 | 3.6571 | 14.1216 | 1.8425 | 0.38206 | 315 | 355 | 3.546
Heyrod | HURST | Heyrod | ASHTON UNDER LYNE C | 1.9211 | 2.446 | 9.8111 | 3.2594 | 0.32866 | 525 | 600 | 2.9883
Huncoat | BLACKBURN RD CLAYTON T12 | Huncoat | ENGLISH ELECTRIC 2 | 0.411 | 0.2574 | 1.2735 | 0.2881 | 0.0228 | 209 | 262 | 0.28663
Huncoat | ENGLISH ELECTRIC | Huncoat | CHURCH | 2.9155 | 4.0229 | 7.527 | 11.5508 | 0.11469 | 262 | 330 | 2.1411
Huncoat | ENGLISH ELECTRIC 1 | Huncoat | BLACKBURN RD CLAYTON T11 | 0.5516 | 0.3454 | 1.71 | 0.3866 | 0.0306 | 590 | 667 | 0.38464
Huncoat | ENGLISH ELECTRIC 1 | Huncoat | GREAT HARWOOD T11 | 2.0782 | 3.1232 | 7.8583 | 8.3612 | 0.04569 | 400 | 400 | 1.529
Huncoat | ENGLISH ELECTRIC 2 | Huncoat | GREAT HARWOOD T12 | 2.0603 | 3.0922 | 7.8426 | 8.2417 | 0.04566 | 400 | 400 | 1.5204
Huncoat | HAMELDON HILL WINDFARM Tee | Huncoat | COG LANE T11 | 2.9318 | 5.6241 | 13.0844 | 16.2013 | 0.26398 | 422 | 530 | 3.621
Huncoat | HAMELDON HILL WINDFARM Tee | Huncoat | HAMELDON HILL WINDFARM | 2.0953 | 2.0394 | 7.8446 | 1.1355 | 0.13486 | 395 | 395 | 1.791
Huncoat | HUNCOAT | Huncoat | COG LANE T12 | 4.878 | 9.6361 | 17.1853 | 35.8014 | 0.27601 | 422 | 530 | 5.024
Huncoat | HUNCOAT | Huncoat | ENGLISH ELECTRIC 1 | 5.9853 | 12.4411 | 11.896 | 62.2261 | 0.0115 | 423 | 500 | 4.159
Huncoat | HUNCOAT | Huncoat | HAMELDON HILL WINDFARM Tee | 1.9686 | 4.0468 | 4.2451 | 19.6052 | 0.015181 | 422 | 530 | 1.438
Huncoat | HUNCOAT | Huncoat | MOORFIELD DRIVE | 4.5906 | 9.4156 | 9.1377 | 44.249 | 0.068283 | 423 | 500 | 3.557
Huncoat | HUNCOAT | Huncoat | STRAWBERRY BANK | 3.7502 | 7.7532 | 7.696 | 38.5245 | 0.00963 | 423 | 530 | 2.626
Huncoat | HUNCOAT | Huncoat | STRAWBERRY BANK | 3.7213 | 7.6993 | 7.606 | 38.2922 | 0.00922 | 423 | 530 | 2.603
Huncoat | HYNDBURN RD T11 | Huncoat | STRAWBERRY BANK | 1.7471 | 1.2243 | 6.3155 | 1.2168 | 0.096384 | 222 | 278 | 1.3135
Huncoat | HYNDBURN RD T12 | Huncoat | STRAWBERRY BANK | 1.263 | 1.3117 | 7.5212 | 0.85483 | 0.067727 | 222 | 278 | 1.2613
Huncoat | KAY ST T11 | Huncoat | CHURCH | 1.7225 | 1.4988 | 6.861 | 1.668 | 0.178 | 341 | 427 | 1.8189
Huncoat | MOORFIELD DRIVE | Huncoat | ENGLISH ELECTRIC 2 | 2.1166 | 4.3064 | 4.0298 | 18.896 | 0.061601 | 423 | 500 | 1.822
Huncoat | NELSON STREET | Huncoat | KAY ST T12 | 2.6259 | 2.5371 | 12.1911 | 3.2083 | 0.327 | 341 | 427 | 3.156
Huncoat | STRAWBERRY BANK | Huncoat | CHURCH | 1.9925 | 1.7337 | 7.9363 | 1.9294 | 0.206 | 296 | 330 | 2.104
Huncoat | STRAWBERRY BANK | Huncoat | NELSON STREET | 1.7177 | 1.704 | 8.805 | 1.4718 | 0.14554 | 365 | 412 | 1.852
Hyde | DUKINFIELD T11 | Hyde | GLOBE LANE STOR | 1.4039 | 1.3664 | 1.9932 | 0.6828 | 0.09036 | 396 | 450 | 1.2
Hyde | HADFIELD A | Hyde | GLOSSOP T11 | 2.2737 | 2.7491 | 3.4503 | 1.4537 | 0.20829 | 400 | 400 | 2.537
Hyde | HATTERSLEY | Hyde | HADFIELD A | 2.1879 | 4.4885 | 10.0022 | 2.1164 | 0.46473 | 530 | 530 | 4.55
Hyde | HATTERSLEY | Hyde | HADFIELD B | 2.3837 | 4.202 | 4.0851 | 1.9261 | 0.41267 | 450 | 550 | 4.16
Hyde | HYDE | Hyde | DUKINFIELD T11 | 1.549 | 2.3574 | 9.2624 | 1.2903 | 0.18234 | 500 | 600 | 2.198
Hyde | HYDE | Hyde | DUKINFIELD T12 | 1.5515 | 2.3621 | 9.3034 | 1.2928 | 0.18314 | 500 | 600 | 2.203
Hyde | HYDE | Hyde | HATTERSLEY | 1.9543 | 4.3082 | 16.9807 | 2.2323 | 0.41602 | 450 | 550 | 4.3429
Hyde | HYDE | Hyde | HATTERSLEY T11 | 1.8372 | 4.0501 | 15.9634 | 2.0985 | 0.3911 | 594 | 660 | 4.0827
Hyde | HYDE | Hyde | HATTERSLEY T12 | 3.628 | 6.9591 | 12.7388 | 25.3502 | 0.1727 | 475 | 530 | 3.614
Hyde | HYDE | Hyde | HYDE T11 | 0.80658 | 0.87979 | 4.241 | 0.9371 | 0.13357 | 400 | 450 | 0.954
Hyde | HYDE | Hyde | HYDE T12 | 0.74912 | 0.77666 | 3.617 | 0.82087 | 0.24989 | 400 | 450 | 1.06
Hyde | HYDE | Hyde | NEWTON T11 | 1.3366 | 1.0634 | 5.1469 | 1.4772 | 0.165 | 378 | 474 | 1.392
Hyde | HYDE | Hyde | NEWTON T12 | 1.3318 | 1.0595 | 5.1284 | 1.4719 | 0.1648 | 378 | 474 | 1.387
Kearsley Local GSP | CARR ST T11 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 6.2824 | 7.596 | 29.2317 | 4.1219 | 0.57552 | 327 | 423 | 7.01
Kearsley Local GSP | CARR ST T12 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 6.2824 | 7.596 | 29.2317 | 4.1219 | 0.57552 | 327 | 423 | 7.01
Kearsley Local GSP | CUTACRE | Kearsley Local GSP | Salford Rd Generation | 0.92253 | 1.6263 | 6.2951 | 0.82754 | 0.15971 | 590 | 667 | 1.61
Kearsley Local GSP | FARNWORTH T11 | Kearsley Local GSP | CAMPBELL ST T11 | 1.5406 | 1.8627 | 2.3378 | 0.98499 | 0.14113 | 535 | 600 | 1.719
Kearsley Local GSP | FARNWORTH T11 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 2.3928 | 2.5212 | 5.8567 | 3.0858 | 0.43066 | 535 | 600 | 3.307
Kearsley Local GSP | FARNWORTH T12 | Kearsley Local GSP | CAMPBELL ST T12 | 1.5446 | 1.8752 | 2.3989 | 0.99143 | 0.14243 | 436 | 485 | 1.732
Kearsley Local GSP | FARNWORTH T12 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 2.4703 | 2.5077 | 5.8885 | 3.0808 | 0.42122 | 535 | 600 | 3.28
Kearsley Local GSP | HILL TOP T13 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 5.3278 | 3.0223 | 8.4022 | 3.769 | 0.43091 | 385 | 435 | 3.918
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | CLIFTON JUNCTION T12 | 5.5529 | 5.6603 | 22.6762 | 5.2143 | 0.46576 | 280 | 380 | 5.043
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | HILL TOP A | 3.1905 | 5.6242 | 5.4678 | 2.578 | 0.55235 | 560 | 760 | 5.568
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | HILL TOP B | 2.8731 | 2.2859 | 23.618 | 1.6164 | 0.9026 | 560 | 760 | 4.3
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | LITTLE HULTON T12 | 7.8275 | 5.0874 | 25.0718 | 5.736 | 0.45823 | 280 | 380 | 5.692
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | MOSS LANE | 9.2241 | 11.4257 | 27.1976 | 38.9785 | 0.43328 | 280 | 380 | 7.2492
Kearsley Local GSP | KEARSLEY LOCAL GSP | Kearsley Local GSP | Salford Rd Generation | 4.7273 | 8.3333 | 32.2575 | 4.2405 | 0.8184 | 590 | 667 | 8.25
Kearsley Local GSP | LITTLE HULTON T11 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 8.4456 | 5.5914 | 27.3329 | 6.2792 | 0.50447 | 245 | 315 | 6.242
Kearsley Local GSP | MOSS LANE T11 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 7.9443 | 5.0497 | 24.8855 | 5.6497 | 0.45575 | 280 | 380 | 5.65
Kearsley Local GSP | RINGLEY T11 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 1.1246 | 0.99842 | 4.5978 | 1.1313 | 0.10328 | 356 | 403 | 1.1511
Kearsley Local GSP | RINGLEY T12 | Kearsley Local GSP | KEARSLEY LOCAL GSP | 1.2704 | 1.1332 | 5.2283 | 1.2886 | 0.11339 | 356 | 403 | 1.2912
Kendal | ARMISTEAD WIND FARM Tee | Kendal | KIRKBY LONSDALE | 12.2548 | 26.3581 | 23.9299 | 127.8964 | 0.05564 | 400 | 400 | 8.755
Kendal | ARNSIDE | Kendal | WHASSET B | 8.0487 | 17.2192 | 16.6176 | 83.5041 | 0.04582 | 480 | 585 | 5.8153
Kendal | BENTHAM | Lancaster | CLAUGHTON | 17.5641 | 30.3347 | 30.8245 | 121.5867 | 0.42955 | 460 | 520 | 13.252
Kendal | INGLETON T11 | Kendal | INGLETON Tee | 3.5828 | 4.9417 | 5.743 | 21.9231 | 0.00508 | 360 | 378 | 1.4336
Kendal | INGLETON Tee | Kendal | BENTHAM | 5.3883 | 7.508 | 8.446 | 33.3997 | 0.00975 | 330 | 330 | 2.1822
Kendal | INGLETON Tee | Nelson | HELWITH BRIDGE | 37.0443 | 50.584 | 56.967 | 210.3161 | 0.04288 | 330 | 330 | 14.5902
Kendal | KENDAL | Kendal | ARMISTEAD WIND FARM Tee | 10.8676 | 21.759 | 22.648 | 99.0067 | 0.3021 | 457 | 502 | 8.772
Kendal | KENDAL | Kendal | LAMBRIGG WINDFARM Tee | 9.64 | 18.4694 | 17.92 | 77.7607 | 0.17241 | 222 | 338 | 7.48
Kendal | KENDAL | Kendal | MINTSFEET T11 | 2.7916 | 2.6967 | 5.413 | 3.4445 | 0.52608 | 465 | 488 | 3.7644
Kendal | KENDAL | Kendal | MINTSFEET T12 / WINDERMERE Tee | 6.3347 | 13.3679 | 13.7953 | 61.4303 | 0.25451 | 560 | 635 | 5.164
Kendal | KENDAL | Kendal | WHASSET A | 28.9481 | 35.2816 | 48.3331 | 108.9499 | 0.22921 | 224 | 307 | 12.1543
Kendal | KENDAL | Kendal | WHASSET B | 29.0642 | 35.4955 | 48.3156 | 109.7378 | 0.22332 | 224 | 307 | 12.1602
Kendal | KENDAL | Kendal | WINDERMERE A | 18.0695 | 30.7562 | 31.9159 | 128.1108 | 0.25931 | 560 | 760 | 17.805
Kendal | KIRKBY LONSDALE | Kendal | MELLING T11 Tee | 24.5561 | 31.4973 | 39.9482 | 107.7957 | 0.14817 | 380 | 414 | 10.179
Kendal | KIRKBY LONSDALE | Kendal | SEDBERGH | 37.7838 | 52.5941 | 59.1237 | 233.9462 | 0.079478 | 380 | 480 | 15.3327
Kendal | LAMBRIGG WINDFARM Tee | Kendal | LAMBRIGG WINDFARM | 0.362 | 0.434 | 2.56 | 0.2417 | 0.0191 | 400 | 450 | 0.40398
Kendal | LAMBRIGG WINDFARM Tee | Kendal | ROAN EDGE | 0.59392 | 1.098 | 1.0848 | 4.3721 | 0.014778 | 590 | 667 | 0.48
Kendal | MELLING T11 Tee | Kendal | BENTHAM | 5.4159 | 7.5521 | 8.432 | 33.6464 | 0.00975 | 380 | 414 | 2.1875
Kendal | MELLING T11 Tee | Kendal | MELLING T11 | 14.1739 | 18.2679 | 20.8837 | 58.6259 | 0.015 | 380 | 414 | 5.346
Kendal | MINTSFEET T12 | Kendal | MINTSFEET T12 / WINDERMERE Tee | 1.056 | 1.4733 | 2.7724 | 3.4111 | 0.063048 | 362 | 400 | 0.984
Kendal | MINTSFEET T12 / WINDERMERE Tee | Kendal | WINDERMERE B | 17.6956 | 38.2705 | 37.52 | 184.0881 | 0.12172 | 480 | 585 | 12.987
Kendal | ROAN EDGE | Kendal | SEDBERGH | 10.5247 | 19.8196 | 27.8415 | 86.4798 | 0.15566 | 222 | 338 | 7.64
Kendal | TROUTBECK BRIDGE SWITCHING STATION | Kendal | AMBLESIDE T11 | 4.6411 | 7.1352 | 8.7492 | 27.7474 | 0.37846 | 412 | 486 | 4.4459
Kendal | TROUTBECK BRIDGE SWITCHING STATION | Kendal | CALGARTH | 3.0626 | 1.6808 | 7.2365 | 1.8809 | 0.088536 | 195 | 250 | 1.4955
Kendal | WINDERMERE A | Kendal | TROUTBECK BRIDGE SWITCHING STATION | 4.8079 | 10.3671 | 9.4965 | 50.8078 | 0.012663 | 580 | 682 | 3.3843
Kendal | WINDERMERE B | Kendal | AMBLESIDE T12 | 16.9985 | 21.4253 | 36.0753 | 80.0443 | 0.29886 | 300 | 361 | 8.8299
Kendal | YEALAND TEE | Kendal | ARNSIDE | 8.2709 | 17.8188 | 16.4251 | 87.4414 | 0.01378 | 371 | 481 | 9.0897
Kendal | YEALAND TEE | Kendal | KIRKBY LONSDALE | 12.7796 | 27.2514 | 26.5261 | 132.1398 | 0.06696 | 371 | 481 | 10.0897
Kendal | YEALAND TEE | Kendal | YEALAND T11 | 2.8348 | 3.9636 | 4.37 | 17.7171 | 0.0031 | 371 | 481 | 11.0897
Lancaster | BROADWAY | Lancaster | BOLTON-LE-SANDS | 3.4332 | 3.5482 | 15.035 | 4.8825 | 0.639 | 600 | 675 | 4.7722
Lancaster | CATON MOOR WINDFARM Tee | Lancaster | QUERNMORE PARK | 5.7115 | 12.2889 | 11.2263 | 60.2312 | 0.01117 | 360 | 414 | 3.9877
Lancaster | CLAUGHTON | Lancaster | CATON MOOR WINDFARM Tee | 3.7065 | 7.5235 | 7.0038 | 35.2389 | 0.031238 | 360 | 414 | 2.6473
Lancaster | LANCASTER | Lancaster | BOLTON-LE-SANDS | 3.331 | 3.5614 | 14.7503 | 4.9059 | 0.66167 | 585 | 661 | 4.8228
Lancaster | LANCASTER | Lancaster | BROADWAY | 2.6649 | 3.3515 | 13.3458 | 4.7697 | 0.65153 | 600 | 675 | 4.7589
Lancaster | LANCASTER | Lancaster | QUERNMORE PARK | 5.6755 | 9.88 | 13.6888 | 43.4759 | 0.11116 | 362 | 500 | 4.1426
Lancaster | LANCASTER | Lancaster | SPRING GARDEN ST T11 | 1.8976 | 2.0793 | 9.0489 | 2.7798 | 0.38594 | 550 | 620 | 2.7886
Lancaster | LANCASTER | Lancaster | SPRING GARDEN ST T12 | 1.9519 | 2.2907 | 14.2001 | 6.7603 | 0.76755 | 550 | 620 | 3.19
Lancaster | LANCASTER | Lancaster | SPRING GARDEN ST T13 | 1.6044 | 2.8283 | 2.7496 | 1.2964 | 0.27776 | 655 | 740 | 2.8
Lancaster | LANCASTER | Lancaster | SPRING GARDEN ST T14 | 0.1 | 3.0294 | 19.992 | 1.4348 | 0.7327 | 655 | 740 | 3.4
Lancaster | LANCASTER | Lancaster | WESTGATE | 4.7791 | 5.4856 | 33.1785 | 15.5354 | 1.7124 | 600 | 675 | 7.47
Lancaster | SPRING GARDEN ST T11 | Lancaster | BURROW BECK T11 | 2.9104 | 2.6179 | 18.6026 | 7.1927 | 0.69009 | 415 | 477 | 3.416
Lancaster | SPRING GARDEN ST T12 | Lancaster | BURROW BECK T12 | 2.892 | 2.5985 | 18.5122 | 7.1334 | 0.68391 | 415 | 477 | 3.389
Lancaster | WOODHILL LANE | Lancaster | BROADWAY | 1.0589 | 1.3114 | 5.3143 | 1.8724 | 0.2493 | 600 | 675 | 1.862
Lancaster | WOODHILL LANE | Lancaster | WESTGATE | 0.461 | 0.5709 | 2.3136 | 0.8152 | 0.1085 | 600 | 675 | 0.81062
Leyland | BOTANY BAY | Leyland | WHITTLE LE WOODS | 2.4536 | 2.5645 | 10.7845 | 3.5301 | 0.46674 | 495 | 500 | 3.4571
Leyland | BOW LANE T12 | Leyland | WHITTLE LE WOODS T12 | 5.801 | 6.456 | 16.9319 | 14.9989 | 0.40965 | 288 | 367 | 4.6583
Leyland | LEYLAND | Leyland | BOW LANE T11 | 1.8526 | 2.0092 | 9.5942 | 2.6547 | 0.2567 | 360 | 452 | 2.4639
Leyland | LEYLAND | Leyland | BOW LANE T12 | 1.3093 | 2.3082 | 2.2439 | 1.058 | 0.2267 | 605 | 680 | 2.2851
Leyland | LEYLAND | Leyland | BUCKSHAW T11 | 4.3718 | 5.2859 | 6.6342 | 2.7952 | 0.4 | 490 | 554 | 4.8781
Leyland | LEYLAND | Leyland | BUCKSHAW T12 | 4.3875 | 5.305 | 6.6581 | 2.8052 | 0.40194 | 490 | 554 | 4.8957
Leyland | LEYLAND | Leyland | HIGHER WALTON | 4.6497 | 7.3311 | 12.0445 | 4.8016 | 0.86142 | 495 | 620 | 7.8572
Leyland | LEYLAND | Leyland | MOSS SIDE (Leyland) T12 | 4.8305 | 2.8141 | 12.285 | 3.3165 | 0.37642 | 315 | 396 | 2.9365
Leyland | LEYLAND | Leyland | SEVEN STARS | 2.1821 | 3.1987 | 28.218 | 1.802 | 0.4659 | 495 | 620 | 3.167
Leyland | LEYLAND | Leyland | WHITTLE LE WOODS | 3.7789 | 6.6616 | 6.4763 | 3.0535 | 0.65422 | 600 | 680 | 6.595
Leyland | LEYLAND | Ribble | BAMBER BRIDGE T11 | 5.1701 | 5.9693 | 12.8882 | 4.0786 | 0.56482 | 360 | 452 | 5.738
Leyland | LEYLAND | Ribble | TARDY GATE | 3.0856 | 3.2979 | 14.5064 | 4.4095 | 0.51907 | 495 | 620 | 4.249
Leyland | RIBBLE | Ribble | HIGHER WALTON | 5.6913 | 5.9297 | 24.8416 | 8.0453 | 1.0427 | 495 | 620 | 7.8778
Longsight | LEVENSHULME | Longsight | LONGSIGHT | 3.7012 | 3.6364 | 7.0453 | 4.6399 | 0.71189 | 470 | 600 | 5.0936
Longsight | LONGSIGHT | Longsight | LEVENSHULME | 2.4782 | 2.4878 | 4.7643 | 3.169 | 0.49234 | 470 | 600 | 3.4936
Longsight | LONGSIGHT | Longsight | LONGSIGHT T11 | 0.012 | 0.0174 | 0.0686 | 0.0215 | 0.002 | 367 | 400 | 0.020481
Longsight | LONGSIGHT | Longsight | LONGSIGHT T12 | 0.0118 | 0.0171 | 0.0674 | 0.0211 | 0.002 | 465 | 525 | 0.020117
Longsight | LONGSIGHT | Longsight | MANCHESTER UNIVERSITY T11 | 1.2606 | 2.2222 | 2.1604 | 1.0186 | 0.2182 | 630 | 630 | 2.2
Longsight | LONGSIGHT | Longsight | MOSS SIDE A (Longsight) | 1.0416 | 1.1757 | 11.1394 | 0.72469 | 0.58269 | 600 | 600 | 2.2669
Longsight | LONGSIGHT | Longsight | MOSS SIDE B (Longsight) | 1.2626 | 1.1695 | 11.6596 | 0.76811 | 0.53743 | 495 | 600 | 2.255
Longsight | LONGSIGHT | Longsight | VICTORIA PARK T11 | 0.1295 | 0.2283 | 0.222 | 0.1046 | 0.0224 | 590 | 649 | 0.22602
Longsight | LONGSIGHT | Longsight | VICTORIA PARK T12 | 0.1346 | 0.2373 | 0.2307 | 0.1088 | 0.0233 | 590 | 649 | 0.23492
Longsight | MANCHESTER UNIVERSITY T11 | Longsight | CIRCLE SQUARE T11 | 0.4455 | 0.98208 | 3.8709 | 0.50886 | 0.094836 | 571 | 678 | 0.99
Longsight | MANCHESTER UNIVERSITY T12 | Longsight | LONGSIGHT | 1.2606 | 2.2222 | 2.1604 | 1.0186 | 0.2182 | 630 | 630 | 2.2
Longsight | MOSS SIDE A (Longsight) | Stretford | CHESTER ROAD B | 1.8429 | 2.1227 | 20.9834 | 1.2104 | 1.082 | 600 | 600 | 4.0548
Lower Darwen | BLACKBURN | Blackburn | BLACKBURN / FENISCOWLES TEE | 7.8353 | 15.5632 | 20.0057 | 55.9451 | 0.13997 | 297 | 372 | 6.439
Lower Darwen | BLACKBURN / FENISCOWLES TEE | Lower Darwen | FENISCOWLES T11 | 7.1705 | 8.55 | 29.0376 | 17.4181 | 0.5404 | 286 | 358 | 7.109
Lower Darwen | EXCHANGE ST 1 | Lower Darwen | INDIA ST T11 | 0.8853 | 1.2805 | 5.056 | 1.5843 | 0.147 | 324 | 406 | 1.5095
Lower Darwen | EXCHANGE STREET T11 | Lower Darwen | EXCHANGE STREET T11 / INDIA ST T12 Tee | 1.6479 | 2.3675 | 9.7114 | 7.4895 | 0.037967 | 378 | 474 | 1.308
Lower Darwen | GOOSE HOUSE LANE | Lower Darwen | EXCHANGE ST 1 | 0.68703 | 1.3319 | 1.9656 | 3.1152 | 0.071561 | 427 | 535 | 0.847
Lower Darwen | GRIFFIN B | Blackburn | RANDAL ST | 1.4611 | 2.5758 | 2.5041 | 1.1806 | 0.25296 | 526 | 660 | 2.55
Lower Darwen | INDIA ST T12 | Lower Darwen | EXCHANGE STREET T11 / INDIA ST T12 Tee | 4.2286 | 7.9095 | 11.7441 | 35.0801 | 0.18353 | 378 | 474 | 3.781
Lower Darwen | LOWER DARWEN | Lower Darwen | ALBION ST T11 | 3.4581 | 5.9915 | 15.791 | 14.4101 | 0.26944 | 400 | 502 | 4.062
Lower Darwen | LOWER DARWEN | Lower Darwen | ALBION ST T12 | 3.4435 | 5.9598 | 15.7301 | 14.2653 | 0.26782 | 400 | 502 | 4.042
Lower Darwen | LOWER DARWEN | Lower Darwen | BLACKBURN / FENISCOWLES TEE | 0.42052 | 0.4128 | 3.5175 | 0.25275 | 0.017983 | 296 | 370 | 0.376
Lower Darwen | LOWER DARWEN | Lower Darwen | EXCHANGE ST 2 | 2.2901 | 4.6931 | 7.3612 | 14.6172 | 0.097697 | 427 | 535 | 2.3414
Lower Darwen | LOWER DARWEN | Lower Darwen | EXCHANGE STREET T11 / INDIA ST T12 Tee | 1.0396 | 1.9639 | 4.0185 | 5.5084 | 0.07083 | 378 | 474 | 1.206
Lower Darwen | LOWER DARWEN | Lower Darwen | GOOSE HOUSE LANE | 2.0549 | 3.9596 | 4.8932 | 11.0516 | 0.13181 | 427 | 535 | 2.037
Lower Darwen | LOWER DARWEN | Lower Darwen | GRIFFIN A | 2.7733 | 4.8889 | 18.9244 | 2.4878 | 0.48013 | 340 | 427 | 4.84
Lower Darwen | LOWER DARWEN | Lower Darwen | GRIFFIN B | 2.7905 | 4.9192 | 19.0417 | 2.5032 | 0.4831 | 340 | 427 | 4.87
Lower Darwen | LOWER DARWEN | Lower Darwen | ROMAN RD T11 | 1.252 | 1.3757 | 6.9528 | 1.9678 | 0.1913 | 378 | 474 | 1.757
Lower Darwen | LOWER DARWEN | Lower Darwen | ROMAN RD T12 | 1.26 | 1.38 | 6.9884 | 1.98 | 0.192 | 378 | 474 | 1.766
Lytham | ANSDELL | Lytham | LYTHAM | 1.17 | 1.2743 | 9.1518 | 1.2147 | 0.4472 | 495 | 620 | 2.0868
Lytham | LYTHAM | Lytham | ST ANNES | 3.6539 | 3.3972 | 20.3029 | 4.01 | 0.81249 | 438 | 550 | 4.987
Lytham | SOUTH PARK | Lytham | LYTHAM | 2.6073 | 2.7443 | 11.4864 | 3.7785 | 0.50293 | 495 | 620 | 3.7048
Lytham | ST THOMAS | Lytham | ANSDELL | 1.6454 | 1.7005 | 7.2055 | 2.34 | 0.30624 | 495 | 620 | 2.2871
Lytham | ST THOMAS | Lytham | LYTHAM | 2.4559 | 2.8117 | 11.1301 | 3.8808 | 0.55311 | 495 | 620 | 3.8571
Lytham | ST THOMAS | Lytham | ST ANNES | 1.3589 | 1.4045 | 5.9513 | 1.9326 | 0.2529 | 495 | 620 | 1.889
Macclesfield GSP | BOLLINGTON | Moss Nook | ALDERLEY | 27.8861 | 26.6701 | 44.5401 | 132.4047 | 0.33498 | 530 | 530 | 10.0964
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | ALDERLEY PARK | 9.4766 | 11.3609 | 66.9601 | 6.3255 | 0.5012 | 460 | 506 | 10.5742
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | ASTRA ZENECA 1 | 0.5545 | 1.0049 | 3.3759 | 1.0453 | 0.1094 | 655 | 655 | 1.0623
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | BOLLINGTON | 4.9374 | 6.1155 | 14.0902 | 9.0677 | 0.41868 | 350 | 350 | 4.9739
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | S.E. MACCLESFIELD | 2.1219 | 2.1929 | 9.2923 | 3.0176 | 0.3949 | 490 | 600 | 2.9495
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | S.E. MACCLESFIELD T12 | 1.3811 | 2.503 | 8.4085 | 2.6035 | 0.2725 | 490 | 600 | 2.6458
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | S.W. MACCLESFIELD | 2.0845 | 2.1543 | 9.1287 | 2.9645 | 0.388 | 490 | 600 | 2.8975
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | WITHYFOLD DRIVE T11 | 0.32826 | 0.28188 | 1.3035 | 0.32472 | 0.034979 | 455 | 519 | 0.3459
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | WITHYFOLD DRIVE T12 | 0.1973 | 0.285 | 1.13 | 0.3531 | 0.0327 | 455 | 519 | 0.33642
Macclesfield GSP | MACCLESFIELD | Macclesfield GSP | WITHYFOLD DRIVE T13 | 0.199 | 0.2879 | 1.1367 | 0.3562 | 0.033 | 455 | 519 | 0.33935
Macclesfield GSP | S.E. MACCLESFIELD | Macclesfield GSP | S.W. MACCLESFIELD | 1.2567 | 1.2988 | 5.5035 | 1.7872 | 0.2339 | 490 | 600 | 1.7469
Moss Nook | ALDERLEY | Moss Nook | ALDERLEY / WILMSLOW TEE | 2.0904 | 3.703 | 3.5885 | 1.6989 | 0.36482 | 450 | 550 | 3.67
Moss Nook | ALDERLEY | Moss Nook | HANDFORTH | 4.9229 | 3.9165 | 18.957 | 5.4408 | 0.60909 | 450 | 550 | 5.127
Moss Nook | ALDERLEY / WILMSLOW TEE | Moss Nook | WILMSLOW | 0.0092 | 0.0073 | 0.0355 | 0.0102 | 0.0011 | 450 | 550 | 0.0096069
Moss Nook | CHELFORD T11 | Moss Nook | ALDERLEY | 29.1596 | 28.0644 | 44.3219 | 142.7884 | 0.050664 | 179 | 220 | 9.1325
Moss Nook | GATLEY / HIGHER MILL T12 Tee | Moss Nook | GATLEY | 0.60028 | 0.54645 | 1.2823 | 0.68468 | 0.10084 | 475 | 600 | 0.748
Moss Nook | GATLEY / HIGHER MILL T12 Tee | Moss Nook | HIGHER MILL T12 | 1.2429 | 1.3608 | 13.0325 | 0.78942 | 0.1626 | 310 | 390 | 1.291
Moss Nook | GATLEY / HIGHER MILL T12 Tee | Moss Nook | MOSS NOOK | 2.489 | 2.2124 | 4.5309 | 2.8467 | 0.40973 | 605 | 680 | 3.06
Moss Nook | HANDFORTH | Moss Nook | MOSS NOOK | 2.7509 | 2.8431 | 12.0474 | 3.9123 | 0.512 | 645 | 746 | 3.8239
Moss Nook | HANDFORTH / WILMSLOW Tee | Moss Nook | HANDFORTH | 1.5853 | 1.6384 | 6.9427 | 2.2546 | 0.2951 | 460 | 540 | 2.2037
Moss Nook | HANDFORTH / WILMSLOW Tee | Moss Nook | WILMSLOW | 3.3902 | 3.2568 | 28.7635 | 1.8556 | 0.1262 | 460 | 540 | 2.907
Moss Nook | MOSS NOOK | Moss Nook | ALDERLEY / WILMSLOW TEE | 2.3827 | 5.052 | 4.37 | 2.3874 | 0.55066 | 450 | 550 | 5.19
Moss Nook | MOSS NOOK | Moss Nook | HANDFORTH / WILMSLOW Tee | 1.4232 | 1.4709 | 6.23 | 2.024 | 0.2649 | 495 | 600 | 1.9783
Moss Nook | MOSS NOOK | Moss Nook | MANCHESTER AIRPORT T11 | 2.0208 | 1.7962 | 3.6786 | 2.3112 | 0.33266 | 475 | 575 | 2.4844
Moss Nook | MOSS NOOK | Moss Nook | MANCHESTER AIRPORT T12 | 1.9968 | 1.7749 | 3.635 | 2.2838 | 0.32871 | 475 | 575 | 2.4549
Moss Nook | MOSS NOOK | Moss Nook | WOODHOUSE PARK | 2.326 | 2.1121 | 4.2738 | 2.7127 | 0.39612 | 475 | 575 | 2.9296
Moss Nook | MOSS NOOK | Sale | BAGULEY | 6.5984 | 6.0301 | 22.2384 | 7.1845 | 0.88388 | 323 | 410 | 7.7328
Moss Nook | THORLEY LANE | Moss Nook | HIGHER MILL T11 | 3.9785 | 3.503 | 16.1161 | 3.9521 | 0.40541 | 310 | 390 | 4.2067
Moss Nook | THORLEY LANE | Moss Nook | THORLEY LANE | 2.1807 | 4.6236 | 18.145 | 2.185 | 0.50397 | 645 | 746 | 4.75
Moss Nook | THORLEY LANE | Moss Nook | THORLEY LANE | 2.1807 | 4.6236 | 18.145 | 2.185 | 0.50397 | 645 | 746 | 4.75
Nelson | NELSON | Nelson | CLOVER HILL T11 | 1.8815 | 1.5497 | 7.3631 | 2.1499 | 0.24638 | 288 | 361 | 2.037
Nelson | NELSON | Nelson | CLOVER HILL T12 | 2.4404 | 2.12 | 9.7204 | 2.3631 | 0.253 | 288 | 361 | 2.577
Nelson | NELSON | Nelson | LANGROYD RD T11 | 4.791 | 5.1443 | 16.8398 | 12.1087 | 0.49079 | 288 | 361 | 4.856
Nelson | NELSON | Nelson | LANGROYD RD T12 | 4.8524 | 5.1153 | 17.1267 | 11.8722 | 0.50147 | 288 | 361 | 4.923
Nelson | NELSON | Nelson | PHILLIPS LANE | 3.3702 | 5.2504 | 7.6317 | 17.7696 | 0.077804 | 363 | 410 | 2.1992
Nelson | NELSON | Nelson | SHUTTLEWOTH HALL PV Tee | 26.31 | 33.0383 | 41.2967 | 101.3965 | 0.19222 | 270 | 310 | 11.097
Nelson | NELSON | Nelson | SPRING COTTAGE T11 | 1.2482 | 1.09 | 4.97 | 1.2086 | 0.129 | 363 | 410 | 1.318
Nelson | NELSON | Nelson | SPRING COTTAGE T12 | 1.2661 | 1.1017 | 5.04 | 1.226 | 0.131 | 363 | 410 | 1.337
Nelson | SETTLE | Nelson | FLAT LANE | 18.5987 | 26.8996 | 29.5082 | 121.5287 | 0.0186 | 307 | 307 | 7.8545
Nelson | SETTLE | Nelson | HELWITH BRIDGE | 10.2928 | 18.05 | 25.8769 | 82.8154 | 0.058184 | 280 | 400 | 6.5211
Nelson | SHUTTLEWOTH HALL PV Tee | Nelson | FLAT LANE | 26.7354 | 34.3883 | 39.43 | 107.5428 | 0.10695 | 270 | 310 | 10.726
New Mills | FERODO T12 | New Mills | NEW MILLS | 9.1288 | 18.44 | 18.7318 | 88.4597 | 0.059162 | 310 | 380 | 6.368
Orrell | KITT GREEN B | Wigan | GIDLOW | 4.047 | 3.5796 | 9.4018 | 4.4634 | 0.6086 | 356 | 490 | 4.812
Orrell | LAMBERHEAD | Orrell | KITT GREEN A | 1.5324 | 1.3621 | 2.7916 | 1.7527 | 0.25227 | 380 | 480 | 1.884
Orrell | ORRELL | Orrell | KITT GREEN A | 1.7124 | 3.6308 | 3.1407 | 1.7158 | 0.39575 | 700 | 763 | 3.73
Orrell | ORRELL | Orrell | KITT GREEN B | 1.7124 | 3.6308 | 3.1407 | 1.7158 | 0.39575 | 700 | 763 | 3.73
Orrell | ORRELL | Orrell | LAMBERHEAD | 2.0628 | 3.6364 | 3.5352 | 1.6668 | 0.35712 | 700 | 763 | 3.6
Orrell | ORRELL | Orrell | UPHOLLAND | 0.39537 | 0.69697 | 0.67758 | 0.31947 | 0.068448 | 245 | 315 | 0.69
Orrell | ORRELL | Orrell | UPHOLLAND | 0.37245 | 0.65657 | 0.6383 | 0.30095 | 0.06448 | 245 | 315 | 0.65
Orrell | WIGAN | Wigan | LAMBERHEAD | 3.812 | 3.322 | 15.2143 | 3.7021 | 0.39098 | 356 | 480 | 4.0159
Orrell | WIGAN | Wigan | LAMBERHEAD | 3.8056 | 3.3158 | 15.232 | 3.6944 | 0.39066 | 356 | 490 | 4.0106
Orrell | AM PAPERMILL T11 | Skelmersdale | PIMBO | 0.50559 | 0.60612 | 3.5728 | 0.33747 | 0.026735 | 513 | 513 | 0.56414
Orrell | ORRELL | Orrell | AM PAPERMILL T11 | 6.747 | 13.6808 | 15.8179 | 59.7715 | 0.20325 | 406 | 505 | 5.7591
Padiham | BOLTON BY BOWLAND | Nelson | FLAT LANE | 13.1473 | 27.4105 | 25.6507 | 137.5972 | 0.02044 | 507 | 575 | 9.0962
Padiham | CLITHEROE WORKS | Padiham | PEEL ST T11 | 2.2347 | 3.9394 | 3.8298 | 1.8057 | 0.38688 | 510 | 575 | 3.9
Padiham | CLITHEROE WORKS | Padiham | RIBBLESDALE | 0.49565 | 0.87374 | 0.84943 | 0.4005 | 0.085808 | 571 | 678 | 0.865
Padiham | PADIHAM | Padiham | PEEL ST T11 | 13.9381 | 25.9743 | 27.0871 | 105.5169 | 0.48867 | 382 | 476 | 12.1093
Padiham | PADIHAM | Padiham | RIBBLESDALE | 17.7849 | 36.3784 | 39.8047 | 163.4767 | 0.15626 | 495 | 530 | 13.307
Padiham | PADIHAM | Padiham | RIBBLESDALE | 21.2798 | 44.2065 | 41.1708 | 204.0612 | 0.11339 | 400 | 450 | 15.446
Padiham | PADIHAM | Padiham | WHALLEY | 3.3999 | 7.2048 | 6.2342 | 3.4045 | 0.78512 | 464 | 525 | 7.401
Padiham | PADIHAM | Padiham | WHALLEY T11 | 6.6421 | 8.0295 | 10.3307 | 4.2472 | 0.60988 | 495 | 620 | 7.411
Padiham | RIBBLESDALE | Padiham | BOLTON BY BOWLAND | 10.4236 | 20.7271 | 24.4332 | 100.6388 | 0.07028 | 365 | 415 | 7.4259
Padiham | WHALLEY | Padiham | RIBBLESDALE | 12.5189 | 24.7543 | 27.6215 | 118.9689 | 0.22541 | 423 | 530 | 9.361
Peel | CLIFTON MARSH Tee | Peel | SALWICK | 1.6249 | 1.4526 | 6.7051 | 1.6406 | 0.16881 | 360 | 414 | 1.7504
Peel | PEEL | Lytham | LYTHAM | 2.2404 | 3.9495 | 15.2881 | 2.0097 | 0.38787 | 575 | 600 | 3.91
Peel | PEEL | Peel | CLIFTON MARSH Tee | 12.6806 | 46.0744 | 26.0469 | 160.6039 | 0.05492 | 360 | 452 | 12.9289
Peel | PEEL | Peel | MERESIDE T11 | 3.51 | 3.047 | 15.3773 | 4.0233 | 0.3116 | 360 | 452 | 3.5398
Peel | PEEL | Peel | MERESIDE T12 | 3.537 | 3.0862 | 15.5571 | 4.0662 | 0.31482 | 243 | 305 | 3.582
Peel | PEEL | Peel | SHEPHERD FM PV Tee | 3.2386 | 10.195 | 6.2247 | 30.939 | 0.15753 | 450 | 565 | 3.92
Peel | PEEL | Peel | STAINING WOOD | 0.99931 | 1.7616 | 1.7126 | 0.80747 | 0.173 | 495 | 620 | 1.744
Peel | PEEL | Peel | WARTON | 6.9501 | 23.5652 | 17.1513 | 79.6245 | 0.14934 | 495 | 620 | 7.5896
Peel | RIBBLE / SALWICK Tee 1 | Peel | STAINING WOOD | 10.2352 | 37.229 | 20.4253 | 129.4053 | 0.047639 | 495 | 620 | 10.4544
Peel | RIBBLE / SALWICK Tee 2 | Peel | HALL CROSS | 4.8807 | 17.6145 | 10.2335 | 61.2121 | 0.030595 | 450 | 565 | 5.018
Peel | SALWICK | Peel | RIBBLE / SALWICK Tee 1 | 0.1301 | 0.20558 | 0.7635 | 0.20367 | 0.035313 | 450 | 565 | 0.231
Peel | SALWICK | Peel | RIBBLE / SALWICK Tee 2 | 0.16599 | 0.26426 | 2.032 | 0.14328 | 0.040624 | 450 | 565 | 0.267
Peel | SHEPHERD FM PV Tee | Peel | HALL CROSS | 3.2704 | 11.7554 | 8.1061 | 40.5001 | 0.041511 | 495 | 620 | 3.3984
Peel | WARTON | Peel | SALWICK | 8.6419 | 26.2991 | 41.0049 | 83.1419 | 0.44018 | 360 | 452 | 9.379
Penrith & Shap | ALSTON T11 | Penrith & Shap | NORTH DYKES | 58.4689 | 75.3572 | 86.1481 | 242.0111 | 0.061801 | 230 | 340 | 22.0529
Penrith & Shap | GALE BAY Tee | Penrith & Shap | NEWBY Tee | 14.2519 | 30.6878 | 28.3438 | 150.0756 | 0.047417 | 430 | 486 | 10.0926
Penrith & Shap | GILLSROW | Stainburn | KESWICK | 11.1339 | 13.3477 | 78.6699 | 7.4317 | 0.589 | 460 | 538 | 12.4234
Penrith & Shap | GREENWAYS | Penrith & Shap | PENRITH | 10.8255 | 13.9064 | 16.5122 | 42.8945 | 0.063204 | 230 | 340 | 4.48
Penrith & Shap | LITTLE SALKELD T11 | Penrith & Shap | GREENWAYS | 18.4381 | 23.7443 | 27.6958 | 75.5472 | 0.040951 | 230 | 340 | 7.105
Penrith & Shap | NEWBIGGIN ON LUNE | Penrith & Shap | KIRKBY STEPHEN | 20.9382 | 26.8842 | 31.4273 | 85.6796 | 0.039051 | 230 | 340 | 8.0286
Penrith & Shap | NEWBY | Penrith & Shap | KIRKBY STEPHEN | 55.1693 | 71.0338 | 82.1958 | 227.4547 | 0.083413 | 230 | 340 | 21.0105
Penrith & Shap | NEWBY | Penrith & Shap | KIRKBY THORE T12 | 18.2481 | 24.7839 | 28.6487 | 109.5719 | 0.05214 | 230 | 340 | 7.4024
Penrith & Shap | NEWBY Tee | Penrith & Shap | NEWBY | 8.0934 | 16.7126 | 15.3463 | 80.2315 | 0.011478 | 275 | 310 | 5.3531
Penrith & Shap | NEWBY Tee | Penrith & Shap | SHAP | 8.3768 | 17.967 | 17.0211 | 87.566 | 0.036141 | 430 | 486 | 5.9813
Penrith & Shap | NORTH DYKES | Penrith & Shap | LITTLE SALKELD T12 | 5.4072 | 6.969 | 7.969 | 22.3652 | 0.0057083 | 230 | 340 | 2.0394
Penrith & Shap | NORTH DYKES | Penrith & Shap | PENRITH | 23.8454 | 30.629 | 35.6919 | 97.4199 | 0.060996 | 230 | 340 | 9.2514
Penrith & Shap | PENRITH | Penrith & Shap | GALE BAY Tee | 5.3723 | 11.5987 | 10.503 | 56.9524 | 0.01081 | 430 | 486 | 3.7611
Penrith & Shap | PENRITH | Penrith & Shap | GILLSROW | 40.6222 | 56.6169 | 62.9627 | 252.3455 | 0.053361 | 253 | 311 | 16.2744
Penrith & Shap | PENRITH | Penrith & Shap | HUTTON END T11 | 21.4945 | 30.4975 | 34.5745 | 139.2602 | 0.045806 | 284 | 351 | 9.942
Penrith & Shap | PENRITH | Penrith & Shap | HUTTON END T12 | 21.3917 | 30.3755 | 34.4241 | 138.7502 | 0.045041 | 284 | 351 | 9.898
Penrith & Shap | PENRITH | Penrith & Shap | NEWBY | 24.3121 | 40.3089 | 41.9589 | 135.0687 | 0.11269 | 460 | 520 | 14.955
Penrith & Shap | SELSMIRE Tee | Penrith & Shap | NEWBIGGIN ON LUNE | 25.5795 | 32.9665 | 37.6893 | 105.7428 | 0.028546 | 230 | 340 | 9.6604
Penrith & Shap | SELSMIRE Tee | Penrith & Shap | SELSMIRE T11 | 0.0562 | 0.0725 | 0.0829 | 0.2326 | 0.0001 | 315 | 355 | 0.021209
Penrith & Shap | SELSMIRE Tee | Penrith & Shap | SHAP | 15.8493 | 24.6951 | 29.2909 | 96.8777 | 0.06346 | 230 | 340 | 8.0508
Penrith & Shap | SHAP | Penrith & Shap | HAWESWATER | 10.4564 | 21.8562 | 20.8983 | 106.0722 | 0.040816 | 380 | 407 | 7.2844
Penrith & Shap | SKELTON C | Penrith & Shap | SKELTON C Tee | 6.2398 | 8.1004 | 15.8149 | 30.6931 | 0.24448 | 284 | 351 | 3.6
Penrith & Shap | WHINFELL T11 Tee | Penrith & Shap | GREENWAYS | 14.2951 | 18.4241 | 21.0623 | 59.1274 | 0.0151 | 230 | 340 | 5.3917
Penrith & Shap | WHINFELL T11 Tee | Penrith & Shap | KIRKBY THORE T11 | 20.4581 | 26.3022 | 30.5184 | 84.1269 | 0.037466 | 230 | 340 | 7.8216
Penrith & Shap | WHINFELL T11 Tee | Penrith & Shap | WHINFELL T11 | 1.9422 | 1.8657 | 16.5 | 1.063 | 0.0723 | 420 | 475 | 1.6654
Preston East | BUSHELL ST | Preston East | PRESTON EAST | 3.6509 | 6.2687 | 11.2168 | 4.0069 | 0.74562 | 605 | 605 | 6.523
Preston East | BUSHELL ST | Ribble | RIBBLE | 1.4626 | 2.5592 | 3.0632 | 1.3084 | 0.39436 | 520 | 650 | 2.82
Preston East | LONGRIDGE T11 Tee | Preston East | LONGRIDGE T11 | 4.0171 | 8.471 | 9.614 | 40.827 | 0.10951 | 420 | 540 | 3.0847
Preston East | LONGRIDGE T12 Tee | Preston East | LONGRIDGE T12 | 4.5731 | 9.0986 | 13.7402 | 36.6296 | 0.14695 | 490 | 554 | 4.064
Preston East | PRESTON EAST | Preston East | AVENHAM | 3.4441 | 5.0496 | 27.0277 | 10.058 | 1.2198 | 485 | 608 | 6.32
Preston East | PRESTON EAST | Preston East | DODGSON RD T11 | 2.5172 | 4.0031 | 16.6229 | 3.1545 | 0.51292 | 360 | 452 | 4.247
Preston East | PRESTON EAST | Preston East | DODGSON RD T12 | 2.6283 | 4.1098 | 17.4805 | 3.523 | 0.55179 | 360 | 452 | 4.402
Preston East | PRESTON EAST | Preston East | LONGRIDGE T11 Tee | 2.9199 | 8.4477 | 8.2165 | 31.4545 | 0.26027 | 660 | 747 | 4.245
Preston East | PRESTON EAST | Preston East | LONGRIDGE T12 Tee | 2.4243 | 6.9172 | 7.0225 | 24.2114 | 0.25827 | 660 | 747 | 3.731
Preston East | PRESTON EAST | Preston East | RIBBLETON T11 | 0.77972 | 2.08 | 8.32 | 1.0193 | 0.23099 | 607 | 753 | 2.178
Preston East | PRESTON EAST | Preston East | RIBBLETON T12 | 0.72244 | 1.9272 | 7.7088 | 0.94442 | 0.21402 | 607 | 753 | 2.018
Preston East | SAMLESBURY T11 | Preston East | LONGRIDGE T11 Tee | 6.2317 | 12.7271 | 12.9344 | 61.327 | 0.041849 | 420 | 540 | 4.387
Preston East | SAMLESBURY T12 | Preston East | LONGRIDGE T12 Tee | 5.1667 | 10.6005 | 10.8587 | 50.8893 | 0.038153 | 330 | 373 | 3.685
Red Bank | ANCOATS NORTH / BLOOM STREET Tee | Bloom Street | BLOOM STREET | 1.77 | 1.475 | 1.5 | 1.2 | 0 | 400 | 400 | 1
Red Bank | ANCOATS NORTH / BLOOM STREET Tee | Red Bank | CANNON ST T13 | 1.7039 | 1.4169 | 6.7657 | 1.6793 | 0.17871 | 310 | 390 | 1.7828
Red Bank | ANCOATS NORTH T14 | Red Bank | REDBANK | 0.629 | 0.9556 | 3.7101 | 0.5232 | 0.0731 | 480 | 506 | 0.88972
Red Bank | BLACKFRIARS A | Red Bank | STRANGEWAYS T11 | 1.2083 | 1.1721 | 2.4065 | 1.4914 | 0.2231 | 400 | 400 | 1.6246
Red Bank | BLOOM STREET | Bloom Street | CANNON ST T11 / BLOOM STREET Tee | 1.6527 | 1.438 | 6.5828 | 1.6003 | 0.171 | 400 | 400 | 1.7452
Red Bank | BLOOM STREET | Bloom Street | CANNON ST T12 / BLOOM STREET Tee | 1.6541 | 1.4393 | 6.5885 | 1.6017 | 0.1712 | 400 | 400 | 1.7467
Red Bank | CANNON ST T11 / BLOOM STREET Tee | Red Bank | CANNON ST T11 | 1.2479 | 1.1054 | 5.0891 | 1.2496 | 0.11641 | 310 | 390 | 1.2823
Red Bank | CANNON ST T12 / BLOOM STREET Tee | Red Bank | CANNON ST T12 | 1.2449 | 1.1029 | 5.0775 | 1.2468 | 0.11608 | 310 | 390 | 1.2791
Red Bank | CANNON ST Tee | Red Bank | ANCOATS NORTH / BLOOM STREET Tee | 4.7192 | 3.776 | 18.6119 | 5.0153 | 0.4514 | 318 | 342 | 4.559
Red Bank | HARPURHEY | Red Bank | NOMA IDNO Tee | 3.7106 | 3.469 | 3.7104 | 2.9486 | 1.3325 | 454 | 576 | 4.8922
Red Bank | HARPURHEY T11 | Red Bank | BLACKLEY T11 | 2.0397 | 1.7879 | 2.0396 | 1.5197 | 0.65395 | 454 | 576 | 2.5075
Red Bank | HARPURHEY T12 | Red Bank | BLACKLEY T12 | 2.0701 | 1.8146 | 2.0701 | 1.5424 | 0.66372 | 454 | 576 | 2.5449
Red Bank | REDBANK | Red Bank | ANCOATS NORTH | 0.61679 | 0.66279 | 0.95576 | 0.55023 | 0.26404 | 500 | 600 | 0.928
Red Bank | REDBANK | Red Bank | ANCOATS NORTH B | 0.57712 | 0.63428 | 1.1546 | 0.51674 | 0.24491 | 500 | 600 | 0.877
Red Bank | REDBANK | Red Bank | BLACKFRIARS A | 1.1656 | 1.3061 | 2.6714 | 1.8142 | 0.27142 | 480 | 600 | 1.8486
Red Bank | REDBANK | Red Bank | HARPURHEY A | 3.692 | 3.4497 | 3.6919 | 2.9323 | 1.3246 | 500 | 500 | 4.8648
Ribble | ASHTON (Ribble) / MOORSIDE Tee | Ribble | MOORSIDE T11 | 4.715 | 6.681 | 18.1157 | 3.5659 | 0.53331 | 490 | 554 | 6.303
Ribble | ASHTON (Ribble) T11 | Ribble | ASHTON (Ribble) / MOORSIDE Tee | 0.0059683 | 0.012654 | 0.010946 | 0.00598 | 0.0013793 | 646 | 745 | 0.013
Ribble | BILSBORROW PV Tee | Ribble | MOORSIDE | 5.8113 | 10.2729 | 10.1346 | 35.2671 | 0.012275 | 345 | 385 | 3.2791
Ribble | BLACKBULL T12 / TULKETH | Ribble | BLACKBULL T12 | 1.6215 | 2.8584 | 2.7789 | 1.3102 | 0.2807 | 605 | 680 | 2.8299
Ribble | BLACKBULL T12 / TULKETH | Ribble | TULKETH | 0.1702 | 0.2428 | 0.8371 | 0.337 | 0.0551 | 495 | 620 | 0.34496
Ribble | BLACKBULL Tee | Preston East | PRESTON EAST | 2.9062 | 4.4279 | 23.4153 | 8.053 | 0.99041 | 495 | 620 | 5.426
Ribble | BLACKBULL Tee | Ribble | BLACKBULL T11 | 1.6782 | 1.8662 | 11.9434 | 5.5341 | 0.59882 | 545 | 600 | 2.574
Ribble | CATTERALL WATERWORKS Tee | Ribble | BILSBORROW PV Tee | 6.8515 | 12.141 | 11.8753 | 41.7463 | 0.011165 | 345 | 385 | 3.85
Ribble | CATTERALL WATERWORKS Tee | Ribble | CATTERALL WATERWORKS T11 | 2.6584 | 5.5659 | 5.4346 | 26.9998 | 0.0153 | 550 | 620 | 1.886
Ribble | GARSTANG T11 | Ribble | CATTERALL WATERWORKS Tee | 5.6372 | 9.8389 | 10.1439 | 33.4934 | 0.02611 | 345 | 385 | 3.25
Ribble | HOLME RD | Peel | RIBBLE / SALWICK Tee 1 | 6.0063 | 20.9784 | 13.3301 | 70.8776 | 0.083838 | 450 | 565 | 6.3903
Ribble | HOLME RD | Ribble | BLACKBULL T12 / TULKETH | 1.1429 | 2.4231 | 2.096 | 1.1451 | 0.264 | 670 | 756 | 2.4894
Ribble | RIBBLE | Peel | RIBBLE / SALWICK Tee 2 | 5.6064 | 19.8419 | 12.654 | 68.4156 | 0.03015 | 450 | 565 | 5.713
Ribble | RIBBLE | Preston East | AVENHAM | 1.3909 | 2.9491 | 2.551 | 1.3937 | 0.321 | 530 | 666 | 3.0297
Ribble | RIBBLE | Preston East | CRAGGS ROW T12 | 1.4947 | 2.546 | 3.3436 | 1.2992 | 0.37869 | 520 | 650 | 2.8
Ribble | RIBBLE | Ribble | ASHTON (Ribble) / MOORSIDE Tee | 2.1403 | 3.4572 | 3.581 | 1.6381 | 0.32424 | 250 | 350 | 3.378
Ribble | RIBBLE | Ribble | BAMBER BRIDGE T11 | 3.2123 | 6.8109 | 5.8915 | 3.2186 | 0.74238 | 671 | 758 | 6.997
Ribble | RIBBLE | Ribble | BAMBER BRIDGE T12 | 5.8428 | 8.1138 | 43.3273 | 10.7305 | 0.68339 | 360 | 452 | 6.535
Ribble | RIBBLE | Ribble | BLACKBULL Tee | 2.7028 | 4.7646 | 4.6321 | 2.184 | 0.46793 | 420 | 475 | 4.717
Ribble | RIBBLE | Ribble | DOUGLAS ST T11 | 1.8094 | 1.4014 | 7.2804 | 1.9461 | 0.15212 | 396 | 400 | 1.66
Ribble | RIBBLE | Ribble | DOUGLAS ST T12 | 2.1844 | 1.8574 | 9.3074 | 2.4178 | 0.18296 | 396 | 400 | 2.1267
Ribble | RIBBLE | Ribble | HOLME RD | 0.27261 | 0.55702 | 0.61555 | 0.29009 | 0.06076 | 650 | 650 | 0.57793
Ribble | RIBBLE | Ribble | HOLME RD T11 | 0.5559 | 0.4837 | 2.2142 | 0.5383 | 0.0575 | 360 | 440 | 0.587
Ribble | RIBBLE | Ribble | HOLME RD T12 | 0.553 | 0.4811 | 2.2025 | 0.5354 | 0.0572 | 360 | 440 | 0.58391
Ribble | RIBBLE | Ribble | MOORSIDE | 4.6017 | 8.1054 | 22.7384 | 4.5071 | 0.79437 | 490 | 554 | 8.068
Ribble | RIBBLE | Ribble | RIBBLE / ST MARYS ST mid-point | 5.2988 | 5.6944 | 26.1323 | 5.9282 | 0.78427 | 494 | 554 | 6
Ribble | RIBBLE | Ribble | ST MARYS ST A | 2.5662 | 3.0124 | 22.4413 | 8.739 | 0.97625 | 505 | 606 | 4.14
Ribble | RIBBLE | Ribble | TARDY GATE | 3.1956 | 3.4042 | 13.7521 | 4.4443 | 0.5798 | 495 | 620 | 4.3415
Ribble | RIBBLE | Ribble | TULKETH | 1.3539 | 2.8108 | 15.5111 | 1.4363 | 0.31199 | 671 | 758 | 2.9433
Ribble | ST MARYS ST B | Ribble | RIBBLE / ST MARYS ST mid-point | 1.4603 | 1.7932 | 2.504 | 0.94841 | 0.13738 | 494 | 554 | 1.659
Rochdale Central | ROCHDALE CENTRAL | Castleton | WOODBINE ST | 1.3924 | 2.4545 | 2.3863 | 1.1251 | 0.24106 | 575 | 600 | 2.43
Rochdale Central | ROCHDALE CENTRAL | Rochdale Central | SPOTLAND | 2.7789 | 2.7078 | 4.0168 | 1.3537 | 0.17979 | 400 | 400 | 2.379
Rochdale Central | ROCHDALE CENTRAL | Rochdale Central | SPOTLAND T12 | 2.5229 | 2.4807 | 4.1681 | 1.2443 | 0.16998 | 250 | 350 | 2.1869
Rochdale Central | ROCHDALE CENTRAL | Rochdale Central | WHITWORTH T12 | 8.981 | 8.7426 | 12.8433 | 4.3706 | 0.57865 | 250 | 350 | 7.679
Rochdale Central | SPOTLAND | Rochdale Central | WHITWORTH T11 | 12.3167 | 14.9647 | 23.8255 | 43.9482 | 0.2295 | 400 | 400 | 6.1217
Rossendale | HAREHOLME T11 / WESLEY PLACE BACUP T11 Tee | Rossendale | HAREHOLME T11 | 0.38649 | 0.31496 | 2.3061 | 0.23412 | 0.019019 | 360 | 452 | 0.30625
Rossendale | HAREHOLME T11 / WESLEY PLACE BACUP T11 Tee | Rossendale | WESLEY PLACE BACUP T11 | 4.728 | 4.0933 | 19.5737 | 4.4426 | 0.46897 | 360 | 452 | 4.894
Rossendale | HAREHOLME T12 / WESLEY PLACE BACUP T12 Tee | Rossendale | HAREHOLME T12 | 0.2337 | 0.2033 | 0.9307 | 0.2263 | 0.0242 | 360 | 452 | 0.24675
Rossendale | PRINNY HILL | Huncoat | NELSON STREET | 10.1134 | 16.8511 | 22.9487 | 54.0139 | 0.12786 | 297 | 392 | 6.4381
Rossendale | PRINNY HILL | Rossendale | GRANE RD | 0.8433 | 0.7338 | 3.3591 | 0.8166 | 0.0873 | 286 | 358 | 0.89054
Rossendale | RAWTENSTALL RD T11 | Rossendale | GRANE RD T11 | 2.5191 | 2.1919 | 10.034 | 2.4393 | 0.2607 | 286 | 358 | 2.6601
Rossendale | RAWTENSTALL RD T12 | Rossendale | GRANE RD T12 | 3.3444 | 3.0776 | 14.8924 | 3.0851 | 0.32004 | 360 | 452 | 3.5621
Rossendale | ROSSENDALE | Rossendale | HAREHOLME T11 / WESLEY PLACE BACUP T11 Tee | 3.47 | 6.5237 | 11.887 | 26.8334 | 0.05873 | 536 | 630 | 2.846
Rossendale | ROSSENDALE | Rossendale | HAREHOLME T12 / WESLEY PLACE BACUP T12 Tee | 3.5627 | 6.6961 | 11.9983 | 27.4621 | 0.057776 | 536 | 630 | 2.8907
Rossendale | ROSSENDALE | Rossendale | RAWTENSTALL RD T11 | 1.0522 | 2.262 | 2.7283 | 10.2743 | 0.00978 | 360 | 452 | 0.87095
Rossendale | ROSSENDALE | Rossendale | RAWTENSTALL RD T12 | 1.0811 | 2.3088 | 3.0959 | 10.2467 | 0.00908 | 360 | 452 | 0.90712
Rossendale | ROSSENDALE | Rossendale | STUBBINS A | 5.7383 | 11.0588 | 16.3818 | 50.0812 | 0.06222 | 537 | 609 | 4.405
Rossendale | ROSSENDALE | Rossendale | STUBBINS B | 5.7787 | 10.9843 | 17.4123 | 48.717 | 0.070658 | 537 | 609 | 4.507
Rossendale | STUBBINS | Bury | HOLT ST | 1.2027 | 2.1202 | 8.2071 | 1.0789 | 0.20822 | 575 | 662 | 2.099
Rossendale | WESLEY PLACE BACUP T12 | Rossendale | HAREHOLME T12 / WESLEY PLACE BACUP T12 Tee | 9.7995 | 16.4932 | 18.4701 | 55.2281 | 0.087724 | 360 | 452 | 5.801
Royton | ROYTON | Royton | HEYSIDE | 1.5805 | 1.8182 | 16.9003 | 1.0305 | 0.2249 | 400 | 450 | 1.731
Royton | ROYTON | Royton | HEYSIDE | 1.3602 | 1.1837 | 5.4679 | 1.5739 | 0.18723 | 400 | 450 | 1.532
Royton | ROYTON | Royton | SHAW T11 | 3.1512 | 3.8216 | 4.7855 | 2.0153 | 0.29065 | 350 | 410 | 3.5295
Royton | ROYTON | Royton | SHAW T12 | 3.138 | 3.7897 | 4.7529 | 2.0093 | 0.28714 | 530 | 645 | 3.4968
Royton | ROYTON | Royton | STOCK LANE | 3.4066 | 4.0814 | 36.2943 | 2.2764 | 0.50683 | 410 | 500 | 3.914
Sale | NORTHENDEN | West Didsbury | NORTHENDEN / WEST DIDSBURY Tee | 0.3413 | 0.297 | 1.3595 | 0.3305 | 0.0353 | 300 | 396 | 0.36043
Sale | SALE | Sale | ASHTON ON MERSEY | 1.6204 | 1.4736 | 2.9793 | 1.8924 | 0.27661 | 475 | 600 | 2.0443
Sale | SALE | Sale | BAGULEY | 5.9384 | 5.1671 | 23.7 | 5.7503 | 0.6145 | 300 | 380 | 6.2708
Sale | SALE | Sale | NORTHENDEN | 5.7329 | 4.9883 | 22.8346 | 5.5513 | 0.5933 | 360 | 405 | 6.0537
Sale | SALE | Sale | SALE MOOR | 2.0897 | 1.9914 | 3.923 | 2.5473 | 0.38368 | 475 | 600 | 2.7792
Sale | SALE | Sale | SALE T11 | 0.70409 | 0.55028 | 6.1221 | 0.35433 | 0.2223 | 480 | 600 | 1.0153
Sale | SALE | Sale | SALE T12 | 0.59592 | 1.0505 | 1.0213 | 0.48152 | 0.10317 | 575 | 600 | 1.04
Sale | SALE MOOR | Sale | ASHTON ON MERSEY | 2.6083 | 2.3185 | 4.7482 | 2.9832 | 0.4294 | 475 | 600 | 3.2067
Sale | SALE MOOR | Sale | BAGULEY | 2.2155 | 2.0588 | 4.1126 | 2.639 | 0.39123 | 475 | 600 | 2.8642
Sandgate | SANDGATE A | Barrow | BARROW (DEVONSHIRE RD) | 1.9823 | 2.1599 | 7.4345 | 2.8547 | 0.3424 | 435 | 457 | 2.8303
Siddick | SIDDICK REACTOR | Siddick | SIDDICK T11 | 0.1 | 8.53 | 0.1 | 7.25 | 0 | N/A | N/A | 1
Siddick | SIDDICK REACTOR | Stainburn | STAINBURN T11 | 3.5276 | 3.7253 | 10.54 | 4.7178 | 0.582 | 425 | 481 | 4.84
Siddick | STAINBURN | Stainburn | SIDDICK | 3.4835 | 8.0122 | 8.5982 | 27.7344 | 0.034493 | 540 | 625 | 2.906
Skelmersdale | AM PAPERMILL T12 | Skelmersdale | SKELMERSDALE | 5.2232 | 7.4774 | 12.5179 | 25.2192 | 0.49053 | 405 | 505 | 5.3884
Skelmersdale | ORMSKIRK | Skelmersdale | SCARISBRICK T11 | 9.1013 | 13.8303 | 18.6171 | 44.5756 | 0.12458 | 284 | 356 | 5.407
Skelmersdale | ORMSKIRK | Wrightington | BURSCOUGH BRIDGE | 5.2301 | 6.1816 | 30.9877 | 3.3792 | 0.60707 | 360 | 452 | 5.79
Skelmersdale | PIMBO | Skelmersdale | WILLOW HEY B | 2.1222 | 1.8863 | 3.8631 | 2.4272 | 0.3493 | 476 | 600 | 2.609
Skelmersdale | SKELMERSDALE | Skelmersdale | ORMSKIRK | 4.0924 | 7.2141 | 7.0134 | 3.3068 | 0.70849 | 495 | 620 | 7.142
Skelmersdale | SKELMERSDALE | Skelmersdale | PIMBO | 2.2465 | 4.0713 | 13.7 | 4.2349 | 0.4433 | 735 | 735 | 4.3037
Skelmersdale | SKELMERSDALE | Skelmersdale | STANLEY WAY | 0.19537 | 0.23623 | 0.29648 | 0.12491 | 0.017898 | 460 | 520 | 0.218
Skelmersdale | SKELMERSDALE | Skelmersdale | WILLOW HEY A | 1.5438 | 1.3723 | 2.81 | 1.7657 | 0.254 | 476 | 540 | 1.898
Skelmersdale | WILLOW HEY B | Skelmersdale | SKELMERSDALE | 2.0986 | 1.8653 | 3.8202 | 2.4002 | 0.3455 | 476 | 565 | 2.58
Spadeadam | ASKERTON CASTLE T11 | Spadeadam | KINKRY HILL T11 | 21.1179 | 27.2216 | 31.1774 | 87.4114 | 0.02394 | 275 | 296 | 7.9941
Spadeadam | KINKRY HILL T11 | Spadeadam | EASTON T11 | 23.4689 | 30.061 | 34.7175 | 96.3371 | 0.02831 | 275 | 296 | 8.8509
Spadeadam | SPADEADAM | Spadeadam | ASKERTON CASTLE T11 | 17.8851 | 23.0493 | 26.3526 | 73.9023 | 0.020796 | 275 | 296 | 6.7614
Stainburn | ANNIE PITT T11 | Stainburn | STAINBURN | 6.3595 | 11.7904 | 17.5222 | 51.4334 | 0.12241 | 360 | 400 | 4.9631
Stainburn | ANNIE PITT T12 | Stainburn | HDA2 Tee | 3.7949 | 6.626 | 10.2934 | 28.2522 | 0.0988 | 373 | 464 | 2.9986
Stainburn | ASPATRIA | Stainburn | TALLENTINE WINDFARM Tee | 10.4059 | 22.491 | 20.2717 | 110.621 | 0.0152 | 460 | 520 | 7.25
Stainburn | ASPATRIA LINE SWITCH | Stainburn | ASPATRIA | 0.05472 | 0.06428 | 0.5016 | 0.03656 | 0.006774 | 190 | 300 | 0.06
Stainburn | ASPATRIA LINE SWITCH | Stainburn | MARYPORT T11 Tee | 22.7483 | 51.1736 | 50.576 | 136.531 | 0.040743 | 190 | 300 | 13.5811
Stainburn | EMBLETON | Stainburn | GREAT CLIFTON Tee | 23.8921 | 53.7376 | 53.1096 | 143.2998 | 0.045933 | 230 | 340 | 14.285
Stainburn | EMBLETON | Stainburn | KESWICK | 29.8861 | 62.0159 | 67.0651 | 286.8681 | 0.46759 | 230 | 340 | 23.01
Stainburn | GREAT CLIFTON Tee | Stainburn | GREAT CLIFTON | 0.093399 | 0.16465 | 0.16007 | 0.075469 | 0.01617 | 475 | 537 | 0.163
Stainburn | HDA1 T11 | Stainburn | LEYLAND NATIONAL T11 / HDA1 Tee | 1.9231 | 4.1565 | 3.75 | 20.4439 | 0.0028 | 309 | 385 | 1.3399
Stainburn | HDA2 Tee | Stainburn | HDA2 T12 | 0.0368 | 0.0796 | 0.0717 | 0.3913 | 0.0001 | 309 | 385 | 0.025644
Stainburn | LEYLAND NATIONAL T11 / HDA1 Tee | Stainburn | LEYLAND NATIONAL T11 | 0.8668 | 1.353 | 4.3291 | 3.6267 | 0.0912 | 370 | 400 | 1.1497
Stainburn | LEYLAND NATIONAL T12 / HDA2 Tee | Stainburn | HDA2 Tee | 0.4308 | 0.5703 | 2.67 | 0.7069 | 0.063 | 480 | 585 | 0.67839
Stainburn | LEYLAND NATIONAL T12 / HDA2 Tee | Stainburn | LEYLAND NATIONAL T12 | 0.0266 | 0.0574 | 0.0517 | 0.2823 | 0 | 367 | 400 | 0.0185
Stainburn | MARYPORT T11 Tee | Stainburn | MARYPORT T11 | 5.0987 | 6.4616 | 7.8491 | 28.3489 | 0.01984 | 190 | 300 | 2.1622
Stainburn | MARYPORT T11 Tee | Stainburn | STAINBURN | 7.2645 | 15.0056 | 13.9947 | 67.2746 | 0.08432 | 323 | 410 | 5.55
Stainburn | MARYPORT T12 | Stainburn | MARYPORT T12 Tee | 5.1306 | 6.5017 | 7.8982 | 28.5299 | 0.01984 | 190 | 300 | 2.1748
Stainburn | MARYPORT T12 Tee | Stainburn | ASPATRIA | 22.768 | 51.1754 | 50.8256 | 136.469 | 0.04195 | 190 | 300 | 13.6014
Stainburn | MARYPORT T12 Tee | Stainburn | FLIMBY WINDFARM Tee | 2.3897 | 4.9882 | 4.6402 | 23.5822 | 0 | 190 | 300 | 1.6572
Stainburn | STAINBURN | Siddick | SIDDICK | 4.0684 | 8.7774 | 9.0759 | 41.4571 | 0.047314 | 480 | 554 | 3.1
Stainburn | STAINBURN | Stainburn | EMBLETON | 26.716 | 59.9768 | 59.2693 | 159.0398 | 0.09085 | 230 | 340 | 16.238
Stainburn | STAINBURN | Stainburn | FLIMBY WINDFARM Tee | 5.1735 | 10.6411 | 9.9347 | 46.641 | 0.08432 | 190 | 300 | 4.1
Stainburn | STAINBURN | Stainburn | GREAT CLIFTON Tee | 2.7757 | 6.1225 | 6.0439 | 15.3618 | 0.047775 | 230 | 340 | 1.944
Stainburn | STAINBURN | Stainburn | LEYLAND NATIONAL T12 / HDA2 Tee | 5.0801 | 10.98 | 9.9 | 54.005 | 0.0074 | 480 | 585 | 3.5394
Stainburn | STAINBURN | Stainburn | WINSCALE WINDFARM Tee | 3.0865 | 6.3914 | 5.9684 | 29.9202 | 0.0053365 | 420 | 475 | 2.165
Stainburn | WHARRELLS HILL WINDFARM Tee | Stainburn | EMBLETON | 8.5694 | 18.5003 | 16.8492 | 90.7482 | 0.024632 | 460 | 520 | 6.017
Stainburn | WHARRELLS HILL WINDFARM Tee | Stainburn | TALLENTINE WINDFARM Tee | 1.9061 | 4.1197 | 3.7132 | 20.2628 | 0.00279 | 460 | 520 | 1.328
Stainburn | WINSCALE WINDFARM | Stainburn | WINSCALE WINDFARM Tee | 0.21344 | 0.25807 | 0.3239 | 0.13647 | 0.01955 | 460 | 520 | 0.23816
Stainburn | WINSCALE WINDFARM Tee | Stainburn | LEYLAND NATIONAL T11 / HDA1 Tee | 3.6404 | 7.5515 | 6.92 | 35.0079 | 0.00547 | 420 | 475 | 2.4267
Stretford | BARTON | Stretford | KELLOGG T11 | 3.9205 | 2.4652 | 12.1646 | 2.7621 | 0.2201 | 256 | 325 | 2.7492
Stretford | BARTON | Stretford | KELLOGG T12 | 3.926 | 2.4657 | 12.2017 | 2.7646 | 0.21893 | 290 | 370 | 2.7493
Stretford | CHESTER ROAD A | Stretford | TRAFFORD | 0.54883 | 0.48955 | 1.1678 | 0.62187 | 0.08412 | 473 | 600 | 0.65725
Stretford | LONGFORD BRIDGE T12 | Stretford | CHESTER ROAD T13 | 0.95806 | 1.6889 | 1.6419 | 0.77414 | 0.16586 | 605 | 680 | 1.672
Stretford | MOSLEY RD T11 | Stretford | TRAFFORD | 1.6463 | 1.9906 | 2.4983 | 1.0526 | 0.15082 | 242 | 307 | 1.837
Stretford | STRETFORD | Stretford | BARTON | 5.0085 | 3.6851 | 19.238 | 5.1428 | 0.39246 | 284 | 360 | 4.3451
Stretford | STRETFORD | Stretford | BARTON | 4.1196 | 3.5805 | 16.4063 | 3.9904 | 0.4256 | 323 | 410 | 4.3453
Stretford | STRETFORD | Stretford | CHESTER ROAD A | 0.89569 | 0.87015 | 8.9587 | 0.52548 | 0.41739 | 495 | 600 | 1.6622
Stretford | STRETFORD | Stretford | CHESTER ROAD B | 0.75693 | 0.87184 | 8.6185 | 0.49712 | 0.44442 | 600 | 600 | 1.6654
Stretford | STRETFORD | Stretford | LONGFORD BRIDGE T11 | 0.0504 | 0.0439 | 0.201 | 0.0488 | 0.0052 | 367 | 400 | 0.053217
Stretford | STRETFORD | Stretford | LONGFORD BRIDGE T12 | 0.0481 | 0.0419 | 0.192 | 0.0466 | 0.005 | 367 | 400 | 0.05084
Stretford | STRETFORD | Stretford | MOSLEY RD T12 | 1.7856 | 1.8575 | 7.7779 | 2.8652 | 0.2409 | 242 | 307 | 2.1048
Stretford | STRETFORD | Stretford | TRAFFORD | 1.4783 | 2.6061 | 2.5336 | 1.1945 | 0.25594 | 504 | 640 | 2.58
Stretford | STRETFORD | Stretford | URMSTON T11 | 3.4466 | 2.9641 | 13.7027 | 3.3483 | 0.35055 | 323 | 400 | 3.5999
Stretford | URMSTON T12 | Stretford | STRETFORD | 3.37 | 2.9003 | 13.4043 | 3.2738 | 0.34277 | 323 | 400 | 3.5202
Stuart Street | ARDWICK T11 / BLOOM STREET Tee | Stuart Street | ARDWICK T11 | 0.62356 | 0.55787 | 2.576 | 0.63597 | 0.054605 | 400 | 504 | 0.63081
Stuart Street | ARDWICK T12 / BLOOM STREET Tee | Stuart Street | ARDWICK T12 | 0.57578 | 0.51513 | 2.3791 | 0.58725 | 0.050412 | 400 | 400 | 0.58247
Stuart Street | BLOOM ST | Bloom St | STUART STREET | 1.9575 | 4.3152 | 17.0085 | 2.2359 | 0.4167 | 575 | 661 | 4.35
Stuart Street | BLOOM ST | Bloom St | STUART STREET | 1.9575 | 4.3152 | 17.0085 | 2.2359 | 0.4167 | 575 | 661 | 4.35
Stuart Street | STUART STREET | Chadderton | NEWTON HEATH B | 2.2246 | 1.4437 | 7.722 | 1.6189 | 0.57645 | 600 | 600 | 2.739
Stuart Street | STUART STREET | Stuart Street | ARDWICK T11 / BLOOM STREET Tee | 3.175 | 2.8202 | 13.0416 | 3.2263 | 0.34098 | 400 | 400 | 3.4401
Stuart Street | STUART STREET | Stuart Street | ARDWICK T12 / BLOOM STREET Tee | 3.1903 | 2.8344 | 13.1089 | 3.2436 | 0.34277 | 290 | 370 | 3.4577
Stuart Street | STUART STREET | Stuart Street | BRADFORD T11 | 1.7398 | 1.4779 | 6.9086 | 1.6965 | 0.17366 | 350 | 400 | 1.7939
Stuart Street | STUART STREET | Stuart Street | BRADFORD T12 | 1.6362 | 1.8546 | 18.1712 | 1.0486 | 0.25128 | 350 | 400 | 1.8
Stuart Street | STUART STREET | Stuart Street | CENTRAL MANCHESTER T11 | 1.7446 | 3.6989 | 3.1996 | 1.748 | 0.40318 | 530 | 600 | 3.8
Stuart Street | STUART STREET | Stuart Street | CENTRAL MANCHESTER T12 | 1.7446 | 3.6989 | 3.1996 | 1.748 | 0.40318 | 530 | 600 | 3.8
Stuart Street | STUART STREET | Stuart Street | EASTLANDS T11 | 0.8551 | 1.0251 | 6.0418 | 0.5707 | 0.0452 | 460 | 538 | 0.95411
Stuart Street | STUART STREET | Stuart Street | EASTLANDS T12 | 0.8476 | 1.0161 | 5.9887 | 0.5657 | 0.0448 | 460 | 538 | 0.94573
Stuart Street | STUART STREET | Stuart Street | MONSALL T11 | 2.7782 | 3.3592 | 4.216 | 1.7763 | 0.25451 | 530 | 600 | 3.1
Stuart Street | STUART STREET | Stuart Street | MONSALL T12 | 2.7782 | 3.3592 | 4.216 | 1.7763 | 0.2545 | 530 | 600 | 3.1
Stuart Street | STUART STREET | Stuart Street | QUEENS PARK T11 | 4.2192 | 3.2279 | 16.3513 | 4.2733 | 0.35298 | 280 | 360 | 3.8295
Stuart Street | STUART STREET | Stuart Street | QUEENS PARK T12 | 2.4945 | 2.2432 | 10.4354 | 2.6073 | 0.27381 | 280 | 360 | 2.7445
Stuart Street | STUART STREET | Stuart Street | STUART ST T11 | 0.1614 | 0.1859 | 1.8377 | 0.106 | 0.023691 | 305 | 390 | 0.17755
Stuart Street | STUART STREET | Stuart Street | STUART ST T12 | 0.1641 | 0.1428 | 0.6536 | 0.1589 | 0.017 | 305 | 390 | 0.17327
Thornton | COPSE RD T11 | Thornton | THORNTON | 6.3759 | 9.135 | 29.949 | 16.9864 | 0.52819 | 360 | 452 | 7.1982
Thornton | JAMESON RD / COPSE RD Tee | Thornton | COPSE RD T12 | 1.7029 | 2.0192 | 11.6968 | 1.3379 | 0.11228 | 360 | 452 | 1.9641
Thornton | JAMESON RD / COPSE RD Tee | Thornton | JAMESON RD T12 | 0.1109 | 0.1329 | 0.783 | 0.074 | 0.0059 | 360 | 452 | 0.12371
Thornton | JAMESON RD / ROSSALL T11 Tee | Thornton | JAMESON RD T11 | 0.87132 | 0.94911 | 4.3331 | 1.4427 | 0.10709 | 360 | 452 | 1.0758
Thornton | JAMESON RD / ROSSALL T11 Tee | Thornton | ROSSALL T11 | 0.9973 | 0.95925 | 3.746 | 1.4855 | 0.092865 | 360 | 452 | 1.003
Thornton | ORCHARD END WINDFARM Tee | Thornton | GARSTANG T12 | 5.8995 | 10.8823 | 11.589 | 52.0631 | 0.033707 | 350 | 385 | 3.707
Thornton | ORCHARD END WINDFARM Tee | Thornton | PREESALL / GARSTANG Tee | 13.4547 | 24.9029 | 24.592 | 122.1586 | 0.02872 | 350 | 385 | 8.089
Thornton | THORNTON | Thornton | JAMESON RD / COPSE RD Tee | 6.2584 | 9.0312 | 24.2416 | 19.4307 | 0.54838 | 360 | 452 | 6.8194
Thornton | THORNTON | Thornton | JAMESON RD / ROSSALL T11 Tee | 5.5194 | 8.2563 | 20.7456 | 18.3259 | 0.44231 | 360 | 452 | 5.8442
Thornton | THORNTON | Thornton | PREESALL T11 | 9.2971 | 16.0279 | 22.205 | 44.5946 | 0.72346 | 365 | 419 | 9.678
Thornton | THORNTON | Thornton | PREESALL T12 | 7.2809 | 12.7999 | 12.7772 | 30.9971 | 0.64086 | 365 | 419 | 8.71
Ulverston | ASKAM T11 | Ulverston | ASKAM T11 / ASKAM WINDFARM Tee | 2.3511 | 5.0676 | 4.651 | 24.8211 | 0.00664 | 460 | 602 | 1.6577
Ulverston | ASKAM T11 / ASKAM WINDFARM Tee | Ulverston | ULVERSTON | 6.8766 | 14.7864 | 13.8105 | 72.1573 | 0.0276 | 460 | 602 | 4.8989
Ulverston | CONISTON T11 | Ulverston | MEAN MOOR PV Tee | 49.741 | 62.0354 | 78.5934 | 194.7987 | 0.24155 | 222 | 352 | 19.884
Ulverston | GRANGE | Ulverston | HAVERTHWAITE | 22.9823 | 29.2972 | 35.8359 | 92.6131 | 0.10336 | 222 | 338 | 9.1925
Ulverston | KIRBY MOOR Tee | Ulverston | HAVERTHWAITE | 21.2938 | 25.8781 | 37.166 | 78.6523 | 0.2401 | 222 | 338 | 9.411
Ulverston | KIRBY MOOR Tee | Ulverston | KIRBY MOOR T11 | 7.2373 | 9.685 | 12.599 | 42.2252 | 0.01559 | 222 | 338 | 2.9096
Ulverston | ULVERSTON | Ulverston | DALTON T12 | 8.0887 | 17.1736 | 16.7662 | 82.5549 | 0.045382 | 342 | 393 | 5.813
Ulverston | ULVERSTON | Ulverston | GLAXO T11 | 3.7928 | 9.8328 | 10.4759 | 31.3751 | 0.1555 | 222 | 338 | 3.8979
Ulverston | ULVERSTON | Ulverston | GLAXO T12 | 3.1377 | 2.7302 | 12.498 | 3.0383 | 0.3247 | 420 | 441 | 3.3133
Ulverston | ULVERSTON | Ulverston | GRANGE | 34.2929 | 41.2398 | 56.2057 | 124.0643 | 0.4058 | 222 | 338 | 15.0021
Ulverston | ULVERSTON | Ulverston | KIRBY MOOR Tee | 9.8924 | 12.6845 | 14.9661 | 40.4239 | 0.026383 | 222 | 338 | 3.8367
Ulverston | ULVERSTON | Ulverston | MEAN MOOR PV Tee | 3.9373 | 4.4181 | 8.9064 | 12.0953 | 0.1157 | 222 | 352 | 2
Vernon Park | HEATON MOOR | Adswood | BRINKSWAY | 2.1029 | 3.7071 | 3.6039 | 1.6992 | 0.36406 | 575 | 662 | 3.67
Vernon Park | HEATON MOOR | Vernon Park | HEATON NORRIS | 1.8253 | 1.4522 | 7.029 | 2.0173 | 0.2258 | 460 | 550 | 1.901
Vernon Park | HEATON NORRIS | Vernon Park | REDDISH VALE T11 | 2.7462 | 2.1847 | 10.5749 | 3.035 | 0.3398 | 450 | 550 | 2.86
Vernon Park | ROMILEY | Vernon Park | WOODLEY | 0.97875 | 2.1576 | 8.5042 | 1.1179 | 0.20835 | 495 | 600 | 2.175
Vernon Park | VERNON PARK | Vernon Park | HEATON MOOR | 4.1874 | 3.6435 | 16.6788 | 4.0547 | 0.433 | 450 | 550 | 4.4217
Vernon Park | VERNON PARK | Vernon Park | HEATON NORRIS | 2.5987 | 2.5674 | 11.167 | 3.4913 | 0.43697 | 495 | 600 | 3.404
Vernon Park | VERNON PARK | Vernon Park | PORTWOOD T11 | 0.93098 | 0.86336 | 8.9964 | 0.53022 | 0.40624 | 310 | 380 | 1.6492
Vernon Park | VERNON PARK | Vernon Park | PORTWOOD T12 | 1.3101 | 1.6771 | 6.9489 | 1.8937 | 0.1877 | 420 | 475 | 1.92
Vernon Park | VERNON PARK | Vernon Park | REDDISH VALE T11 | 6.4793 | 7.0879 | 12.6443 | 20.2525 | 0.11062 | 350 | 350 | 3.054
Vernon Park | VERNON PARK | Vernon Park | REDDISH VALE T12 | 6.5797 | 7.1508 | 12.9562 | 20.3229 | 0.11619 | 350 | 350 | 3.124
Vernon Park | VERNON PARK | Vernon Park | ROMILEY | 2.6402 | 2.7287 | 11.5623 | 3.7548 | 0.4914 | 495 | 620 | 3.67
Vernon Park | VERNON PARK | Vernon Park | WOODLEY | 1.708 | 1.7943 | 8.0022 | 2.4956 | 0.30309 | 495 | 600 | 2.3801
West Didsbury | CHORLTON | West Didsbury | WHALLEY RANGE | 1.8237 | 1.9357 | 7.4651 | 2.6227 | 0.29724 | 470 | 600 | 2.5246
West Didsbury | DIDSBURY | West Didsbury | FALLOWFIELD | 2.1161 | 3.7303 | 3.6265 | 1.7099 | 0.36635 | 575 | 662 | 3.693
West Didsbury | NORTHENDEN / WEST DIDSBURY Tee | Moss Nook | WOODHOUSE PARK | 4.118 | 3.9898 | 15.5503 | 4.6834 | 0.5328 | 300 | 396 | 4.9656
West Didsbury | NORTHENDEN / WEST DIDSBURY Tee | West Didsbury | WEST DIDSBURY | 2.6521 | 4.6752 | 4.5452 | 2.143 | 0.4591 | 575 | 600 | 4.6285
West Didsbury | WEST DIDSBURY | West Didsbury | CHORLTON | 1.7488 | 1.5874 | 3.2085 | 2.0388 | 0.29765 | 465 | 590 | 2.2016
West Didsbury | WEST DIDSBURY | West Didsbury | CHRISTIE | 2.8938 | 3.4989 | 4.3914 | 1.8502 | 0.2651 | 465 | 520 | 3.229
West Didsbury | WEST DIDSBURY | West Didsbury | CHRISTIE | 2.8938 | 3.4989 | 4.3914 | 1.8502 | 0.2651 | 465 | 520 | 3.229
West Didsbury | WEST DIDSBURY | West Didsbury | DIDSBURY | 2.6271 | 2.3491 | 4.7805 | 2.9992 | 0.4326 | 455 | 510 | 3.238
West Didsbury | WEST DIDSBURY | West Didsbury | FALLOWFIELD | 1.6395 | 3.4686 | 3.0044 | 1.6386 | 0.37767 | 470 | 600 | 3.562
West Didsbury | WEST DIDSBURY | West Didsbury | NORTHERNDEN | 2.4221 | 4.2697 | 4.1509 | 1.9571 | 0.41932 | 575 | 662 | 4.227
West Didsbury | WEST DIDSBURY | West Didsbury | WEST DIDSBURY T11 | 1.0096 | 1.2207 | 1.532 | 0.6455 | 0.0925 | 400 | 490 | 1.1265
West Didsbury | WEST DIDSBURY | West Didsbury | WEST DIDSBURY T12 | 1.0083 | 1.2191 | 1.5301 | 0.6447 | 0.0924 | 400 | 531 | 1.1251
West Didsbury | WEST DIDSBURY | West Didsbury | WHALLEY RANGE | 1.1417 | 0.91702 | 10.1069 | 0.58481 | 0.37858 | 465 | 590 | 1.6969
West Didsbury | WEST DIDSBURY | West Didsbury | WITHINGTON | 1.6101 | 2.9179 | 9.8025 | 3.0351 | 0.3177 | 370 | 600 | 3.0845
West Didsbury | WEST DIDSBURY T11 | West Didsbury | BENCHILL | 5.5241 | 4.6786 | 21.6408 | 5.2853 | 0.49931 | 250 | 295 | 5.4636
West Didsbury | WHALLEY RANGE | Longsight | MOSS SIDE B (Longsight) | 1.7406 | 1.397 | 14.9156 | 0.93613 | 0.56638 | 465 | 590 | 2.6066
West Didsbury | WITHINGTON | West Didsbury | DIDSBURY | 1.6955 | 2.9889 | 2.9057 | 1.37 | 0.29353 | 400 | 400 | 2.959
Westhoughton | GREEN ST T13 | Wigan | WIGAN | 0.41959 | 0.4467 | 1.9558 | 0.53145 | 0.042338 | 356 | 403 | 0.49665
Westhoughton | MOSS LANE GENERATION | Westhoughton | CROWN LANE T11 | 0.70478 | 1.386 | 2.286 | 5.365 | 0.034984 | 356 | 490 | 0.678
Westhoughton | WESTHOUGHTON | Westhoughton | CROWN LANE T12 | 9.3399 | 16.4292 | 19.3332 | 70.7997 | 0.18456 | 400 | 400 | 6.3447
Westhoughton | WESTHOUGHTON | Westhoughton | LOSTOCK T11 | 1.502 | 2.722 | 9.1442 | 2.8313 | 0.2964 | 605 | 680 | 2.8773
Westhoughton | WESTHOUGHTON | Westhoughton | LOSTOCK T12 | 2.1465 | 2.0426 | 4.0269 | 2.613 | 0.39322 | 485 | 565 | 2.85
Westhoughton | WESTHOUGHTON | Westhoughton | MOSS LANE GENERATION | 7.3378 | 14.431 | 17.7131 | 62.9433 | 0.2329 | 356 | 490 | 6.1418
Westhoughton | WESTHOUGHTON | Westhoughton | WIGAN | 8.5292 | 14.5841 | 30.3404 | 33.8055 | 0.6769 | 356 | 400 | 10.2851
Westhoughton | WIGAN | Westhoughton | GREEN ST T11 | 0.4138 | 0.5003 | 0.6279 | 0.2645 | 0.0379 | 356 | 403 | 0.46168
Wigan | GIDLOW | Wrightington | STANDISH | 5.6429 | 7.7142 | 13.4715 | 21.2619 | 0.35036 | 356 | 450 | 4.7066
Wigan | WIGAN | Westhoughton | GREEN ST T12 | 0.41772 | 0.44627 | 1.9519 | 0.53112 | 0.04238 | 356 | 403 | 0.49644
Wigan | WIGAN | Wigan | GIDLOW | 1.6129 | 2.9196 | 9.81 | 3.0372 | 0.317 | 500 | 500 | 3.0869
Wigan | WIGAN | Wigan | GIDLOW | 1.615 | 2.9233 | 9.823 | 3.041 | 0.31747 | 515 | 600 | 3.0908
Wigan | WIGAN | Wigan | WORSLEY MESNES T11 | 1.3126 | 1.1771 | 5.556 | 1.2391 | 0.13042 | 356 | 484 | 4.0897
Wigan | WIGAN | Wigan | WORSLEY MESNES T12 | 1.3082 | 1.1774 | 5.5646 | 1.2426 | 0.12754 | 356 | 484 | 5.0897
Wrightington | CHORLEY SOUTH T12 | Wrightington | WOODFIELD RD | 1.1575 | 2.0404 | 1.9836 | 0.93526 | 0.20038 | 495 | 620 | 2.02
Wrightington | HANGING BRIDGE | Wrightington | BURSCOUGH BRIDGE | 5.712 | 4.9701 | 22.7515 | 5.531 | 0.591 | 360 | 452 | 6.0317
Wrightington | HANGING BRIDGE | Wrightington | TARLETON | 6.1461 | 9.952 | 18.0364 | 38.8209 | 0.28775 | 360 | 452 | 5.5195
Wrightington | WOODFIELD RD | Leyland | BOTANY BAY | 1.2 | 1.3185 | 6.6635 | 1.886 | 0.183 | 495 | 620 | 1.6839
Wrightington | WRIGHTINGTON | Wrightington | BURSCOUGH BRIDGE | 17.8253 | 30.669 | 34.1854 | 106.0319 | 0.16851 | 360 | 452 | 10.8243
Wrightington | WRIGHTINGTON | Wrightington | CHORLEY SOUTH T11 | 8.2286 | 11.3743 | 27.356 | 28.1034 | 0.88041 | 495 | 565 | 8.6447
Wrightington | WRIGHTINGTON | Wrightington | CHORLEY SOUTH T12 | 3.7474 | 6.606 | 6.4223 | 3.028 | 0.64877 | 495 | 565 | 6.54
Wrightington | WRIGHTINGTON | Wrightington | HANGING BRIDGE | 14.5996 | 29.2425 | 29.5229 | 138.3107 | 0.092488 | 400 | 500 | 10.1106
Wrightington | WRIGHTINGTON | Wrightington | STANDISH | 5.1446 | 9.4023 | 17.4041 | 30.3928 | 0.58488 | 356 | 450 | 5.959
Wrightington | WRIGHTINGTON | Wrightington | TARLETON | 20.87 | 41.704 | 48.759 | 200.5346 | 0.2717 | 420 | 550 | 15.6787
Wrightington | WRIGHTINGTON | Wrightington | WOODFIELD RD | 8.7707 | 17.7654 | 16.3858 | 63.8751 | 0.52598 | 420 | 550 | 9.245
Wrightington | WRIGHTINGTON | Wrightington | WRIGHTINGTON T11 | 1.4695 | 2.5815 | 3.6679 | 11.6154 | 0.042783 | 360 | 452 | 7.0897
Wrightington | WRIGHTINGTON | Wrightington | WRIGHTINGTON T12 | 1.4707 | 2.5668 | 3.6936 | 11.4939 | 0.044287 | 360 | 452 | 8.0897

## 132kV Circuit Data - Published
132kV CIRCUIT DATA
From Substation Group | Node 1 | To Substation Group | Node 2 | Resistance % | Reactance % | Zero Seq Resistance % | Zero Seq Reactance % | Susceptance % | Continuous (or Summer for OHL) Rating (Amps) | Cyclic (or Winter for OHL) Rating (Amps) | Length (km)
Kearsley GSP | Agecroft GT1 / Frederick Rd GT1 Tee | Kearsley GSP | Frederick Rd 1 | 0.17653 | 0.22188 | 1.3636 | 0.44944 | 6.0939 | 568.6025 | 656.0799 | 3.604
Kearsley GSP | Agecroft GT2 / Frederick Rd GT2 Tee | Kearsley GSP | Frederick Rd 2 | 0.16994 | 0.22929 | 1.3327 | 0.43901 | 5.694 | 568.6025 | 656.0799 | 3.583
Kearsley GSP | Atherton 1 / Westhoughton 1 Tee | Kearsley GSP | Atherton 1 | 0.004984 | 0.011732 | 0.0469 | 0.01498 | 0.1073 | 594.9769 | 644.9702 | 0.14
Kearsley GSP | Atherton 1 / Westhoughton 1 Tee | Kearsley GSP | Westhoughton 1 | 0.24075 | 0.64699 | 1.3626 | 1.4963 | 7.1496 | 672.7005 | 726.9802 | 6.02
Kearsley GSP | Atherton 2 / Westhoughton 2 Tee | Kearsley GSP | Atherton 2 | 0.002136 | 0.005028 | 0.0201 | 0.00642 | 0.045984 | 594.9769 | 644.9702 | 0.06
Kearsley GSP | Atherton 2 / Westhoughton 2 Tee | Kearsley GSP | Westhoughton 2 | 0.24075 | 0.64699 | 1.3626 | 1.4963 | 7.1496 | 672.7005 | 726.9802 | 6.02
Carrington GSP | BARTON 1 | Carrington GSP | Tenax 1 | 0.20212 | 0.24145 | 1.0257 | 0.34375 | 1.9569 | 341.1615 | 399.99 | 2.75
Carrington GSP | BARTON 2 | Carrington GSP | Tenax 2 | 0.20212 | 0.24145 | 1.0257 | 0.34375 | 1.9569 | 341.1615 | 399.99 | 2.75
Stanah GSP | BISPHAM 2 | Penwortham West GSP | Penwortham West GSP | 0.85019 | 5.6952 | 2.9059 | 13.7767 | 0.952 | 1109.9559 | 1219.9586 | 25.95
Penwortham East GSP | BLACKBURN 1 | Padiham GSP | Padiham | 0.31616 | 1.9998 | 1.0886 | 5.3542 | 0.5238 | 631.5862 | 687.0031 | 9.49
Penwortham East GSP | BLACKBURN 2 | Padiham GSP | Padiham | 0.50054 | 2.092 | 1.2822 | 5.3174 | 1.0115 | 631.5862 | 687.0031 | 9.49
Penwortham East GSP | Blackburn | Penwortham East GSP & Rochdale GSP | LOWER DARWEN 1 | 0.93188 | 2.3925 | 2.2029 | 6.2916 | 0.84954 | 433.0127 | 537.9855 | 10.76
Bold | BOLD | Bold | Golborne 2 / Parkside 2 Tee | 0.7001 | 1.7842 | 1.8299 | 4.7426 | 0.52882 | 433.0127 | 537.9855 | 8.196
Kearsley GSP | BOLTON 1 | Rochdale GSP | Scout Moor Tee | 1.3082 | 3.2985 | 3.297 | 8.2201 | 2.5906 | 433.0127 | 537.9855 | 15
Bredbury GSP | BREDBURY GSP | Bredbury GSP | HAZEL GROVE 1 | 0.276 | 0.3367 | 2.1638 | 0.701 | 9.4944 | 587.0165 | 587.0165 | 5.52
Bredbury GSP | BREDBURY GSP | Bredbury GSP | HAZEL GROVE 2 | 0.2745 | 0.3349 | 2.1521 | 0.6972 | 9.4428 | 587.0165 | 587.0165 | 5.49
Bredbury GSP | BREDBURY GSP | Bredbury GSP | EDGELY Tee | 0.17496 | 0.25385 | 1.5409 | 0.49555 | 8.5044 | 570.0022 | 619.9998 | 4.34
Padiham GSP / Rochdale GSP | Burnley Tee | Padiham GSP / Rochdale GSP | BURNLEY 2 | 0.2853 | 0.7291 | 0.67521 | 1.9717 | 0.1572 | 433.0127 | 537.9855 | 3.17
Kearsley GSP | BURY 2 | Kearsley GSP | Radcliffe 2 Tee | 0.29657 | 1.6049 | 0.72217 | 3.5253 | 1.5541 | 629.8367 | 761.0526 | 7.75
Carrington GSP | Barton / Shell Tee | Carrington GSP | BARTON 3 | 0.23482 | 0.58831 | 1.6995 | 0.86513 | 4.6452 | 433.0127 | 537.9855 | 6.292
Carrington GSP | Carrington GSP | Carrington GSP | Barton / Shell Tee | 0.0012768 | 0.0043491 | 0.0012768 | 0.0036967 | 0.053044 | 709.9659 | 774.9615 | 0.057
Carrington GSP | Carrington GSP | Carrington GSP | Altrincham 1 / Sale 1 Tee | 0.081845 | 0.51805 | 0.24834 | 1.3274 | 0.56326 | 814.9824 | 890.1691 | 2.74
Carrington GSP | Carrington GSP | Carrington GSP | BARTON 1 | 0.44628 | 1.156 | 1.4237 | 2.7244 | 2.3276 | 433.0127 | 537.9855 | 6.815
Carrington GSP | Carrington GSP | Carrington GSP | BARTON 2 | 0.44628 | 1.156 | 1.4237 | 2.7244 | 2.3276 | 433.0127 | 537.9855 | 6.815
Carrington GSP | Carrington GSP | Carrington GSP | Altrincham 2 / Sale 2 Tee | 0.081845 | 0.51805 | 0.24834 | 1.3274 | 0.56326 | 814.9824 | 890.1691 | 2.74
Carrington GSP | Carrington GSP | Carrington GSP | CARRINGTON GT1 | 0.008736 | 0.029757 | 0.008736 | 0.025293 | 0.36293 | 709.9659 | 774.9615 | 0.39
Carrington GSP | Carrington GSP | Carrington GSP | CARRINGTON GT2 | 0.01008 | 0.034335 | 0.01008 | 0.029185 | 0.41877 | 709.9659 | 774.9615 | 0.45
Harker GSP & Hutton GSP | CARLISLE NORTH 2 | Harker GSP & Hutton GSP | HARKER GSP | 0.05376 | 0.10536 | 0.4476 | 0.15 | 0.85392 | 499.0581 | 604.9056 | 1.2
Rochdale GSP | Castleton 2 | Rochdale GSP | Rochdale (Dane St) | 0.25011 | 0.61042 | 0.76767 | 1.6171 | 1.503 | 433.0127 | 537.9855 | 3.17
Penwortham East GSP | Catterall 1 | Penwortham East GSP | Catterall Tee 1 | 0.4626 | 1.1902 | 1.043 | 2.8539 | 0 | 433.0127 | 537.9855 | 5.14
Penwortham East GSP | Catterall Tee 1 | Penwortham East GSP | BLACKBURN 1 | 2.1861 | 5.6353 | 4.0384 | 12.6498 | 0 | 572.9764 | 647.3321 | 24.29
Penwortham East GSP | Catterall Tee 2 | Penwortham East GSP | BLACKBURN 2 | 2.1861 | 5.6353 | 4.0384 | 12.6498 | 0 | 572.9764 | 647.3321 | 24.29
Penwortham East GSP | Catterall Tee 2 | Penwortham East GSP | Catterall 2 | 0.4626 | 1.1902 | 1.043 | 2.8539 | 0 | 433.0127 | 537.9855 | 5.14
Rochdale GSP | Cliviger Tee | Padiham GSP / Rochdale GSP | BURNLEY 1 | 0.8667 | 2.2245 | 2.0705 | 5.9128 | 0.4776 | 433.0127 | 537.9855 | 9.63
Rochdale GSP | Rochdale (Dane St) | Rochdale GSP | ROCHDALE GSP | 0.39565 | 1.0352 | 0.91225 | 2.6712 | 1.2516 | 433.0127 | 537.9855 | 5.16
Harker GSP & Hutton GSP | Seaton 1 Tee | Harker GSP & Hutton GSP | HARKER GSP | 2.7115 | 11.5622 | 6.4973 | 29.7751 | 2.7064 | 822.2867 | 931.6334 | 51.16
Harker GSP & Hutton GSP | Seaton 2 Tee | Harker GSP & Hutton GSP | HARKER GSP | 2.929 | 12.427 | 7.0979 | 31.6627 | 3.1215 | 728.9922 | 728.9922 | 55.29
Stalybridge GSP | Droylsden 1 Tee | Stalybridge GSP | DROYLSDEN 1 | 0.079377 | 0.11171 | 0.69095 | 0.23095 | 3.6169 | 586.098 | 655.9924 | 1.893
Stalybridge GSP | Droylsden 1 Tee | Stalybridge GSP | Stuart St 3 | 0.18 | 0.494 | 0.414 | 1.208 | 0 | 433.0127 | 537.9855 | 2
Stalybridge GSP | Droylsden / Stuart St Tee | Stalybridge GSP | DROYLSDEN 2 | 0.08091 | 0.11407 | 0.70445 | 0.23546 | 3.6918 | 586.098 | 655.9924 | 1.93
Stalybridge GSP | Droylsden / Stuart St Tee | Stalybridge GSP | Stuart St 2 | 0.18 | 0.494 | 0.414 | 1.208 | 0 | 433.0127 | 537.9855 | 2
Bredbury GSP | EDGELY Tee | Bredbury GSP | ADSWOOD 1 | 0.029849 | 0.043678 | 0.26408 | 0.084328 | 1.465 | 570.0022 | 619.9998 | 0.746
Harker GSP & Hutton GSP | Egremont 1 | Harker GSP & Hutton GSP | SELLAFIELD | 1.0674 | 2.7278 | 2.5262 | 7.3769 | 0.5883 | 433.0127 | 537.9855 | 11.86
Harker GSP & Hutton GSP | Egremont 2 | Harker GSP & Hutton GSP | SELLAFIELD | 1.0674 | 2.7278 | 2.5262 | 7.3769 | 0.5883 | 433.0127 | 537.9855 | 11.86
Bold | Golborne 1 | Bold | Golborne 1 / Parkside 1 Tee | 0.3303 | 0.8441 | 0.78171 | 2.2827 | 0.182 | 433.0127 | 537.9855 | 3.67
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | Belle Vue 1 Tee | 0.3096 | 1.1751 | 0.5676 | 2.9233 | 0.46784 | 866.0254 | 1075.971 | 6.88
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | CARLISLE 1 | 0.4986 | 1.2853 | 1.108 | 2.9694 | 0.2748 | 433.0127 | 537.9855 | 5.54
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | STAINBURN / EGREMONT TEE | 4.5863 | 11.8532 | 10.2494 | 27.4548 | 2.6885 | 433.0127 | 537.9855 | 51.16
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | CARLISLE 2 | 0.65521 | 1.6811 | 1.547 | 4.405 | 0.36109 | 433.0127 | 537.9855 | 7.2801
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | Spadeadam 2 | 2.331 | 5.9473 | 5.5504 | 16.0772 | 1.5107 | 433.0127 | 537.9855 | 25.95
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | CARLISLE NORTH 1 | 0.0538 | 0.1054 | 0.4476 | 0.15 | 0.8539 | 499.0581 | 604.9056 | 1.2
Harker GSP & Hutton GSP | Harker GSP | Harker GSP & Hutton GSP | Spadeadam 1 | 2.337 | 5.9547 | 5.5933 | 16.0917 | 1.7055 | 433.0127 | 537.9855 | 26.06
Harker GSP & Hutton GSP | Belle Vue 1 Tee | Harker GSP & Hutton GSP | CARLISLE 3 | 0.2187 | 0.56376 | 0.486 | 1.3025 | 0.1205 | 433.0127 | 537.9855 | 2.43
Harker GSP & Hutton GSP | Belle Vue 1 Tee | Harker GSP & Hutton GSP | Penrith 1 | 2.6312 | 6.9955 | 4.8238 | 17.3989 | 0 | 433.0127 | 537.9855 | 30.67
Harker GSP & Hutton GSP | Belle Vue 2 Tee | Harker GSP & Hutton GSP | Egremont 1 | 5.8212 | 14.9843 | 12.2067 | 35.5909 | 0 | 433.0127 | 537.9855 | 64.68
Harker GSP & Hutton GSP | Belle Vue 2 Tee | Harker GSP & Hutton GSP | HARKER GSP | 0.3096 | 1.1751 | 0.5676 | 2.9233 | 0.4678 | 866.0254 | 1075.971 | 6.88
Harker GSP & Hutton GSP | Belle Vue 2 Tee | Harker GSP & Hutton GSP | Penrith 2 | 2.6362 | 7.0036 | 6.2056 | 18.2766 | 0.263 | 433.0127 | 537.9855 | 30.8
Heysham GSP | Heysham GSP | Heysham GSP | Trimpell 1 | 0.1111 | 0.2716 | 0.37858 | 0.68616 | 0.8008 | 572.9764 | 647.3321 | 1.42
Heysham GSP | Heysham GSP | Heysham GSP | LANCASTER 1 | 0.41473 | 1.5398 | 0.89389 | 3.8168 | 1.7301 | 687.0031 | 687.0031 | 9.35
Heysham GSP | Heysham GSP | Heysham GSP | LANCASTER 2 | 0.41081 | 1.5417 | 0.87697 | 3.809 | 1.8681 | 687.0031 | 687.0031 | 9.35
Heysham GSP | Heysham GSP | Heysham GSP | Trimpell 2 | 0.1463 | 0.3683 | 0.39883 | 0.97402 | 0.364 | 572.9764 | 647.3321 | 1.71
Stalybridge GSP | Hartshead 2 | Stalybridge GSP | STALYBRIDGE GSP | 0.04004 | 0.1041 | 0.08555 | 0.2463 | 0.22854 | 433.0127 | 537.9855 | 0.61
Padiham GSP | Huncoat 2 | Padiham GSP | Padiham | 0.20992 | 0.52555 | 0.5598 | 1.4101 | 0.55631 | 433.0127 | 537.9855 | 2.45
Hutton GSP | Hutton GSP | Hutton GSP | KENDAL 2 | 0.5526 | 1.4183 | 1.3262 | 3.7515 | 0.3045 | 572.9764 | 647.3321 | 6.14
Hutton GSP | Hutton GSP | Hutton GSP | Natland Tee 2 | 0.30263 | 1.2848 | 0.73088 | 3.2718 | 0.3021 | 822.2867 | 931.6334 | 5.71
Hutton GSP | Hutton GSP | Hutton GSP | Kendal / Penrith Tee | 0.4752 | 1.2197 | 1.1405 | 3.2261 | 0.2619 | 572.9764 | 647.3321 | 5.28
Hutton GSP | Hutton GSP | Hutton GSP | Natland Tee 1 | 0.30263 | 1.2848 | 0.73088 | 3.2718 | 0.3021 | 822.2867 | 931.6334 | 5.71
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Atherton 2 / Westhoughton 2 Tee | 0.34637 | 2.657 | 1.058 | 6.3958 | 3.2416 | 814.9824 | 890.1516 | 13.63
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Atherton 1 / Westhoughton 1 Tee | 0.3573 | 2.5361 | 1.142 | 6.162 | 1.6208 | 814.9824 | 890.1516 | 13.63
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Agecroft GT3 / Frederick Rd GT3 Tee | 0.40322 | 0.97587 | 1.4947 | 2.4327 | 5.0523 | 572.9764 | 647.3321 | 6.206
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Agecroft GT1 / Frederick Rd GT1 Tee | 0.51057 | 1.3586 | 1.1816 | 3.3967 | 1.8765 | 572.9764 | 647.3321 | 7.042
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | BOLTON 3 | 0.3668 | 1.7756 | 0.77275 | 4.2938 | 1.0748 | 866.0254 | 1075.971 | 10.34
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | BOLTON 4 | 0.36596 | 1.7808 | 0.74198 | 4.3126 | 0.71079 | 866.0254 | 1075.971 | 10.28
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Radcliffe 1 Tee | 0.059131 | 0.2951 | 0.13301 | 0.79374 | 0.21873 | 743.5572 | 922.8857 | 1.44
Kearsley GSP | KEARSLEY GSP | Kearsley GSP | Agecroft GT2 / Frederick Rd GT2 Tee | 0.39815 | 0.96675 | 1.48 | 2.3732 | 5.3267 | 572.9764 | 647.3321 | 6.349
Hutton GSP | KENDAL 1 | Hutton GSP | Kendal / Penrith Tee | 0.0774 | 0.19866 | 0.18576 | 0.52546 | 0.0427 | 572.9764 | 647.3321 | 0.86
Hutton GSP | Kendal / Penrith Tee | Hutton GSP | Shap 1 | 2.0511 | 5.2645 | 4.9226 | 13.9247 | 0 | 537.9855 | 537.9855 | 22.79
Kirkby GSP | KIRKBY GSP | Kirkby GSP | ORRELL 2 | 0.58634 | 2.203 | 2.3154 | 8.3689 | 4.4784 | 769.8004 | 835.4083 | 13.302
Penwortham West GSP | Leyland 1 Tee | Penwortham West GSP | LEYLAND 1 | 0.2223 | 0.57057 | 0.53352 | 1.5092 | 0 | 572.9764 | 647.3321 | 2.47
Penwortham West GSP | Leyland 1 Tee | Wrightington | WRIGHTINGTON | 1.1214 | 2.8964 | 2.6732 | 7.6251 | 0.61802 | 433.0127 | 537.9855 | 12.46
Penwortham West GSP | Leyland 2 Tee | Penwortham West GSP | LEYLAND 2 | 0.2223 | 0.57057 | 0.53352 | 1.5092 | 0 | 572.9764 | 647.3321 | 2.47
Penwortham West GSP | Leyland 2 Tee | Wrightington | WRIGHTINGTON | 1.1205 | 2.894 | 2.6711 | 7.619 | 0.61752 | 433.0127 | 537.9855 | 12.45
Harker GSP & Hutton GSP | Lindal Tee 1 | Hutton GSP | BARROW (DEVONSHIRE RD) 1 | 0.8253 | 2.1274 | 1.834 | 4.9151 | 0.4548 | 433.0127 | 537.9855 | 9.17
Harker GSP & Hutton GSP | Lindal Tee 1 | Harker GSP & Hutton GSP | Rooscote | 0.7659 | 1.9573 | 1.8126 | 5.2932 | 0.4221 | 433.0127 | 537.9855 | 8.51
Harker GSP & Hutton GSP | Lindal Tee 2 | Harker GSP & Hutton GSP | Rooscote | 0.7659 | 1.9573 | 1.8126 | 5.2932 | 0.422 | 433.0127 | 537.9855 | 8.51
South Manchester GSP | Moss Nook 1 | South Manchester GSP | SOUTH MANCHESTER GSP | 0.33519 | 0.48261 | 2.9613 | 0.9772 | 16.0208 | 570.0022 | 619.9998 | 8.233
South Manchester GSP | Moss Nook 2 | South Manchester GSP | SOUTH MANCHESTER GSP | 0.37555 | 0.52296 | 3.2341 | 1.0771 | 16.6294 | 534.9981 | 585.0002 | 8.804
South Manchester GSP | Moss Nook 3 | South Manchester GSP | SOUTH MANCHESTER GSP | 0.31678 | 0.45632 | 2.7997 | 0.92367 | 15.1518 | 570.0022 | 619.9998 | 7.785
Hutton GSP | Natland Tee 1 | Hutton GSP | LANCASTER 3 | 2.367 | 6.0753 | 5.6545 | 16.1482 | 1.3045 | 433.0127 | 537.9855 | 26.3
Hutton GSP | Natland Tee 1 | Hutton GSP | Ulverston 1 Tee | 1.608 | 6.8568 | 3.8532 | 17.6579 | 1.605 | 822.2867 | 931.6334 | 30.34
Hutton GSP | Natland Tee 2 | Hutton GSP | Ulverston 1 Tee | 1.608 | 6.8568 | 3.8532 | 17.6579 | 1.605 | 822.2867 | 931.6334 | 30.34
Padiham GSP / Rochdale GSP | NELSON 2 | Padiham GSP / Rochdale GSP | Burnley Tee | 0.7497 | 1.9242 | 1.7909 | 5.1146 | 0.4132 | 433.0127 | 537.9855 | 8.33
Stalybridge GSP | New Mills Tee 1 | Stalybridge GSP | BUXTON 1 | 0.97605 | 3.076 | 1.746 | 6.909 | 0 | 520.49 | 647.3321 | 13.39
Stalybridge GSP | New Mills Tee 1 | Stalybridge GSP | NEW MILLS 1 | 0.027 | 0.069 | 0.0639 | 0.187 | 0.0149 | 433.0127 | 537.9855 | 0.3
Stalybridge GSP | New Mills Tee 2 | Stalybridge GSP | BUXTON 2 | 0.97605 | 3.076 | 1.746 | 6.909 | 0 | 520.49 | 647.3321 | 13.39
Stalybridge GSP | New Mills Tee 2 | Stalybridge GSP | NEW MILLS | 0.027 | 0.069 | 0.0639 | 0.1866 | 0.0149 | 433.0127 | 537.9855 | 0.3
Stalybridge GSP | New Mills Tee 2 | Stalybridge GSP | STALYBRIDGE GSP | 1.4815 | 3.8354 | 3.6082 | 9.8505 | 4.77 | 572.9764 | 647.3321 | 19.37
Kirkby GSP | ORRELL 2 | Washway Farm GSP | WIGAN 2 | 0.83032 | 2.1476 | 2.148 | 5.6029 | 1.2785 | 572.9764 | 647.3321 | 9.695
Padiham GSP | Padiham | Padiham GSP | Padiham | 0 | 0.01 | 0.0236 | -0.42965 | 0 | 1150.0205 | 1150.0205 | 0.53
Bold | Golborne 1 / Parkside 1 Tee | Bold | Bold | 0.74304 | 1.8989 | 1.7585 | 5.1352 | 0 | 433.0127 | 537.9855 | 8.256
Bold | Golborne 2 / Parkside 2 Tee | Bold | Golborne 2 | 0.3303 | 0.8441 | 0.78171 | 2.2827 | 0.182 | 433.0127 | 537.9855 | 3.67
Stanah GSP | Peel | Penwortham West GSP / Stanah GSP | BLACKPOOL 1 | 0.37291 | 0.89163 | 0.67918 | 1.8199 | 4.0134 | 433.0127 | 537.9855 | 6.67
Stanah GSP | Peel | Penwotham West GSP / Stanah | Lytham 1 | 0.2448 | 0.6256 | 0.57936 | 1.6918 | 0.1349 | 433.0127 | 537.9855 | 2.72
Stanah GSP | Peel | Stanah GSP | STANAH GSP | 0.52352 | 3.4628 | 1.6853 | 8.9384 | 0.40232 | 1049.7278 | 1255.2994 | 16.05
Stanah GSP | Peel | Penwortham West GSP / Stanah GSP | BLACKPOOL 2 | 0.37291 | 0.89163 | 0.67918 | 1.8199 | 4.0134 | 433.0127 | 537.9855 | 6.67
Stanah GSP | Peel | Penwotham West GSP / Stanah | Lytham 2 | 0.2448 | 0.6256 | 0.57936 | 1.6918 | 0.1349 | 433.0127 | 537.9855 | 2.72
Harker GSP & Hutton GSP | Penrith 1 | Hutton GSP | Shap 1 | 2.3436 | 6.0152 | 5.5986 | 15.9886 | 1.2916 | 433.0127 | 537.9855 | 26.04
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP & Rochdale GSP | Private | 0.0090944 | 0.030978 | 0.0090944 | 0.026331 | 0.37782 | 634.2105 | 782.922 | 0.406
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP | Catterall Tee 1 | 1.4022 | 3.5872 | 3.3124 | 9.6726 | 0.18612 | 572.9764 | 647.3321 | 15.73
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP | Catterall Tee 2 | 1.4085 | 3.6033 | 3.3273 | 9.7162 | 0.18612 | 572.9764 | 647.3321 | 15.8
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP | Ribble 2 | 0.17646 | 0.43245 | 0.52443 | 1.1505 | 0.84439 | 433.0127 | 537.9855 | 2.16
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP | Preston East 2 | 0.25312 | 0.86219 | 0.25312 | 0.73286 | 10.5158 | 626.8012 | 681.7982 | 11.3
Penwortham East GSP | Penwotham East GSP | Penwortham East GSP | Preston East 1 | 0.25312 | 0.86219 | 0.25312 | 0.73286 | 10.5158 | 626.8012 | 681.7982 | 11.3
Penwortham West GSP | PENWORTHAM WEST GSP | Penwortham West GSP | Leyland 2 Tee | 0.17235 | 0.68614 | 0.49058 | 1.5891 | 2.898 | 1064.9488 | 1170.0091 | 4.49
Penwortham West GSP | PENWORTHAM WEST GSP | Penwortham West GSP | Leyland 1 Tee | 0.17475 | 0.70234 | 0.53377 | 1.6033 | 3.542 | 1064.9488 | 1170.0091 | 4.69
Penwortham West GSP | PENWORTHAM WEST GSP | Stanah GSP | Peel | 0.53361 | 3.5752 | 1.8444 | 8.6324 | 1.02 | 1110.0871 | 1219.8711 | 16.37
Kearsley GSP | Radcliffe 1 | Kearsley GSP | Radcliffe 1 Tee | 0.0549 | 0.15616 | 0.12322 | 0.36539 | 0 | 428.6388 | 537.9855 | 0.61
Kearsley GSP | Radcliffe 2 | Kearsley GSP | Radcliffe 2 Tee | 0.063 | 0.17516 | 0.16802 | 0.40614 | 0.209 | 428.6388 | 537.9855 | 0.76
Kearsley GSP | Radcliffe 1 Tee | Kearsley GSP | BURY 1 | 0.29657 | 1.6049 | 0.72217 | 3.5253 | 1.5541 | 629.8367 | 761.0526 | 7.75
Kearsley GSP | Radcliffe 2 Tee | Kearsley GSP | KEARSLEY GSP | 0.05865 | 0.29271 | 0.13255 | 0.79195 | 0.18425 | 743.5572 | 922.8857 | 1.41
Penwortham East GSP | Ribble 3 | Penwortham East GSP | Penwotham East GSP | 0.18135 | 0.43635 | 0.553 | 1.1581 | 0.92479 | 433.0127 | 537.9855 | 2.22
Rochdale GSP | Rochdale GSP | Penwortham East GSP & Rochdale GSP | LOWER DARWEN 2 | 2.5509 | 6.5363 | 6.0436 | 16.6368 | 1.6074 | 433.0127 | 537.9855 | 28.59
Rochdale GSP | Rochdale GSP | Stalybridge GSP | BELFIELD 1 | 0.33844 | 0.41441 | 2.6618 | 0.86407 | 11.7505 | 587.0165 | 587.0165 | 6.806
Rochdale GSP | Rochdale GSP | Stalybridge GSP | BELFIELD 2 | 0.33894 | 0.41576 | 2.6684 | 0.86652 | 11.7797 | 587.0165 | 587.0165 | 6.823
Rochdale GSP | Rochdale GSP | Rochdale GSP | Todmorden Tee 1 | 1.1236 | 2.8857 | 2.6749 | 7.6359 | 0.82569 | 433.0127 | 537.9855 | 12.65
Rochdale GSP | Rochdale GSP | Rochdale GSP | Todmorden Tee 2 | 1.1239 | 2.8865 | 2.6752 | 7.6366 | 0.83445 | 433.0127 | 537.9855 | 12.66
Rochdale GSP | Rochdale GSP | Rochdale GSP | Castleton 1 | 0.4595 | 1.1758 | 1.0794 | 3.149 | 0.43392 | 433.0127 | 537.9855 | 5.25
Harker GSP & Hutton GSP | Rooscote | Harker GSP & Hutton GSP | Sandgate 2 | 0.081 | 0.20944 | 0.20298 | 0.49291 | 0.15 | 440.0109 | 440.0109 | 0.89
Harker GSP & Hutton GSP | Rooscote | Hutton GSP | BARROW (DEVONSHIRE RD) 2 | 0.20416 | 0.44247 | 1.2761 | 0.86263 | 2.1526 | 433.0127 | 481.0596 | 3.76
Harker GSP & Hutton GSP | Rooscote | Hutton GSP | Ulverston 1 Tee | 0.6466 | 2.7534 | 1.5532 | 7.0664 | 0.64538 | 822.2867 | 931.6334 | 12.2
Padiham GSP | Rossendale 1 | Padiham GSP | Padiham | 1.155 | 2.9426 | 2.7854 | 7.9484 | 1.0005 | 572.9764 | 647.3321 | 12.93
Carrington GSP | Altrincham 1 / Sale 1 Tee | Carrington GSP | ALTRINCHAM 1 | 0.41598 | 1.055 | 1.2409 | 2.734 | 1.0607 | 433.0127 | 537.9855 | 5.24
Carrington GSP | Altrincham 1 / Sale 1 Tee | Carrington GSP | Sale 1 | 0.12283 | 0.78055 | 0.4371 | 2.0846 | 0.3995 | 809.9524 | 899.0044 | 3.753
Carrington GSP | Altrincham 2 / Sale 2 Tee | Carrington GSP | ALTRINCHAM 2 | 0.42414 | 1.0675 | 1.3008 | 2.7541 | 1.0244 | 433.0127 | 537.9855 | 5.4
Carrington GSP | Altrincham 2 / Sale 2 Tee | Carrington GSP | Sale 2 | 0.12283 | 0.78055 | 0.4371 | 2.0846 | 0.3995 | 809.9524 | 899.0044 | 3.753
Harker GSP & Hutton GSP | Siddick Tee | Harker GSP & Hutton GSP | Seaton 1 Tee | 0.0225 | 0.0575 | 0.04125 | 0.14775 | 0 | 433.0127 | 537.9855 | 0.25
Harker GSP & Hutton GSP | Siddick Tee | Harker GSP & Hutton GSP | SELLAFIELD | 2.745 | 7.015 | 6.4965 | 18.971 | 1.5128 | 433.0127 | 537.9855 | 30.5
Harker GSP & Hutton GSP | Siddick Tee | Harker GSP & Hutton GSP | Siddick 1 | 0.324 | 0.8352 | 0.72 | 1.9296 | 0.1786 | 433.0127 | 537.9855 | 3.6
Harker GSP & Hutton GSP | SELLAFIELD | Harker GSP & Hutton GSP | Lindal Tee 1 | 3.5857 | 10.9458 | 7.1242 | 28.0249 | 0 | 621.0889 | 708.5662 | 47.18
Harker GSP & Hutton GSP | SELLAFIELD | Harker GSP & Hutton GSP | Lindal Tee 2 | 3.5857 | 10.9458 | 7.1242 | 28.0249 | 0 | 621.0889 | 708.5662 | 47.18
South Manchester GSP | South Manchester GSP | South Manchester GSP | BLOOM ST 1 | 0.3967 | 0.541 | 3.363 | 1.127 | 16.6796 | 534.9981 | 585.0002 | 9.016
South Manchester GSP | South Manchester GSP | South Manchester GSP | West Didsbury 2 | 0.23676 | 0.17467 | 1.2313 | 0.43129 | 3.7725 | 337.0064 | 337.0064 | 2.59
South Manchester GSP | South Manchester GSP | South Manchester GSP | Stretford 2 | 0.18389 | 0.29384 | 1.7601 | 0.56218 | 11.096 | 594.9988 | 650.0002 | 5.254
South Manchester GSP | South Manchester GSP | South Manchester GSP | West Didsbury 3 | 0.050995 | 0.2303 | 0.050995 | 0.19576 | 3.7818 | 890.1691 | 890.1691 | 3.29
South Manchester GSP | South Manchester GSP | South Manchester GSP | BLOOM ST 2 | 0.4007 | 0.5464 | 3.3969 | 1.1384 | 16.848 | 534.9981 | 585.0002 | 9.107
Harker GSP & Hutton GSP | Stainburn 2 | Harker GSP & Hutton GSP | Seaton 2 Tee | 0.2475 | 0.6325 | 0.45375 | 1.6252 | 0 | 433.0127 | 537.9855 | 2.75
Harker GSP & Hutton GSP | Stainburn 2 | Harker GSP & Hutton GSP | SELLAFIELD | 2.5191 | 6.4377 | 5.9619 | 17.4098 | 1.3883 | 433.0127 | 537.9855 | 27.99
Stanah GSP | STANAH GSP | Stanah GSP | Thornton 1 | 0.072 | 0.184 | 0.1704 | 0.4976 | 0.0397 | 433.0127 | 537.9855 | 0.8
Stanah GSP | STANAH GSP | Stanah GSP | Thornton 2 | 0.0774 | 0.1978 | 0.18318 | 0.53492 | 0.0427 | 433.0127 | 537.9855 | 0.86
Stanah GSP | STANAH GSP | Stanah GSP | BISPHAM 1 | 0.19353 | 1.2728 | 0.61533 | 3.2584 | 0.40232 | 1049.7278 | 1255.2994 | 6.05
Stalybridge GSP | Stalybridge GSP | Stalybridge GSP | New Mills Tee 1 | 1.4813 | 3.7014 | 3.9691 | 9.9381 | 3.3797 | 572.9764 | 647.3321 | 17.42
Stalybridge GSP | Stalybridge GSP | Stalybridge GSP | Droylsden 1 Tee | 0.4479 | 2.2373 | 1.0254 | 6.1474 | 0.58549 | 734.8094 | 861.6515 | 10.29
Stalybridge GSP | Stalybridge GSP | Stalybridge GSP | Hartshead 1 | 0.03976 | 0.1033 | 0.08527 | 0.24562 | 0.21979 | 433.0127 | 537.9855 | 0.6
Stalybridge GSP | Stalybridge GSP | Stalybridge GSP | Droylsden / Stuart St Tee | 0.44787 | 2.2373 | 1.0254 | 6.1474 | 0.5855 | 734.8094 | 861.6515 | 10.29
Stalybridge GSP | Stalybridge GSP | Stalybridge GSP | Hyde 2 | 0.57945 | 1.4867 | 2.0796 | 3.5851 | 4.0536 | 433.0127 | 537.9855 | 8.88
Stalybridge GSP | Stuart St / Hyde Tee | Stalybridge GSP | Hyde 1 | 0.54554 | 1.321 | 1.7089 | 3.507 | 3.1902 | 433.0127 | 537.9855 | 6.9
Stalybridge GSP | Stuart St / Hyde Tee | Stalybridge GSP | Stuart St 1 | 1.0611 | 2.7129 | 2.5906 | 7.2271 | 0.74962 | 433.0127 | 537.9855 | 11.91
South Manchester GSP | Stretford 1 | South Manchester GSP | SOUTH MANCHESTER GSP | 0.18266 | 0.29226 | 1.7484 | 0.55843 | 11.0127 | 594.9988 | 650.0002 | 5.219
Rochdale GSP | Todmorden Tee 1 | Rochdale GSP | Cliviger Tee | 0.36 | 0.924 | 0.86 | 2.456 | 0.1984 | 433.0127 | 537.9855 | 4
Rochdale GSP | Todmorden Tee 2 | Padiham GSP / Rochdale GSP | Burnley Tee | 0.9414 | 2.4163 | 2.2489 | 6.4224 | 0.5188 | 433.0127 | 537.9855 | 10.46
Hutton GSP | Ulverston 1 Tee | Harker GSP & Hutton GSP | Rooscote | 0.6519 | 2.7759 | 1.566 | 7.1237 | 0.65067 | 822.2867 | 931.6334 | 12.3
Hutton GSP | Ulverston 1 Tee | Hutton GSP | Ulverston 1 | 0.03326 | 0.13402 | 0.10092 | 0.336 | 0.0865 | 585.0002 | 481.0596 | 0.64
Hutton GSP | Ulverston 1 Tee | Hutton GSP | Ulverston 2 | 0.02968 | 0.12656 | 0.07112 | 0.32592 | 0.0296 | 822.2867 | 931.6334 | 0.56
Bredbury GSP | BREDBURY GSP | Bredbury GSP | LONGSIGHT1 | 0.3935 | 0.585 | 3.5012 | 1.0897 | 20.2 | 681.0109 | 681.0109 | 10.09
Bredbury GSP | BREDBURY GSP | Bredbury GSP | ADSWOOD 2 | 0.18744 | 0.26858 | 1.6422 | 0.5358 | 8.8954 | 604.3808 | 655.9924 | 4.58
Bredbury GSP | BREDBURY GSP | Bredbury GSP | LONGSIGHT 2 | 0.393 | 0.5841 | 3.4943 | 1.09 | 20.14 | 681.0109 | 681.0109 | 10.07
Washway Farm GSP | Washway Farm GSP | Washway Farm GSP | Skelmersdale 2 / Wigan 2 Tee | 0.01656 | 0.062854 | 0.03036 | 0.15636 | 0.025 | 866.0254 | 1075.971 | 0.368
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Redbank 2 | 0.9126 | 2.102 | 3.1288 | 5.5062 | 6.4434 | 433.0127 | 537.9855 | 11.7
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Royton 2 | 0.80172 | 2.0488 | 1.8974 | 5.5408 | 0.4418 | 433.0127 | 537.9855 | 8.908
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Greenhill 2 | 0.25572 | 0.34214 | 2.1541 | 0.72222 | 10.4527 | 624.9817 | 624.9817 | 5.713
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | CHADDERTON 2 | 0.0109 | 0.0176 | 0.102 | 0.0342 | 0.5656 | 728.9922 | 728.9922 | 0.28
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | CHADDERTON 1 | 0.007 | 0.0113 | 0.0657 | 0.022 | 0.364 | 728.9922 | 728.9922 | 0.18
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Greenhill 3 | 0.25025 | 0.33803 | 2.1206 | 0.70696 | 10.4563 | 624.9817 | 624.9817 | 5.663
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Royton 1 | 0.80172 | 2.0488 | 1.8974 | 5.5408 | 0.4418 | 433.0127 | 537.9855 | 8.908
Whitegate GSP | WHITEGATE GSP | Whitegate GSP | Redbank 3 | 0.5253 | 0.6398 | 3.7245 | 1.2606 | 16.9035 | 602.9811 | 602.9811 | 9.55
Washway Farm GSP | Skelmersdale 1 / Wigan 1 Tee | Washway Farm GSP | Skelmersdale 1 | 0.0441 | 0.16738 | 0.08085 | 0.4164 | 0.0666 | 866.0254 | 1075.971 | 0.98
Washway Farm GSP | Skelmersdale 1 / Wigan 1 Tee | Washway Farm GSP | Washway Farm GSP | 0.01656 | 0.062854 | 0.03036 | 0.15636 | 0.025 | 866.0254 | 1075.971 | 0.368
Washway Farm GSP | Skelmersdale 1 / Wigan 1 Tee | Washway Farm GSP | WIGAN 1 | 1.7849 | 4.5696 | 4.5164 | 12.0115 | 1.7717 | 572.9764 | 647.3321 | 20.321
Washway Farm GSP | Skelmersdale 2 / Wigan 2 Tee | Washway Farm GSP | ORRELL 1 | 0.9367 | 2.4088 | 2.2891 | 6.3501 | 0.19747 | 572.9764 | 647.3321 | 10.555
Washway Farm GSP | Skelmersdale 2 / Wigan 2 Tee | Washway Farm GSP | Skelmersdale 2 | 0.0441 | 0.16738 | 0.08085 | 0.4164 | 0.0666 | 866.0254 | 1075.971 | 0.98
Kearsley GSP | Agecroft GT3 / Frederick Rd GT3 Tee | Kearsley GSP | Frederick Rd 3 | 0.25897 | 0.53853 | 0.9965 | 1.2152 | 3.1348 | 529.2377 | 612.3412 | 3.682
Harker GSP & Hutton GSP | STAINBURN / EGREMONT TEE | Harker GSP & Hutton GSP | Egremont 2 | 1.7167 | 4.4061 | 4.12 | 11.6542 | 0.94607 | 572.9764 | 647.3321 | 19.074
Harker GSP & Hutton GSP | STAINBURN / EGREMONT TEE | Harker GSP & Hutton GSP | Stainburn 1 | 0.022176 | 0.043461 | 0.18463 | 0.061875 | 0.35224 | 481.1252 | 585.0045 | 0.495
Penwortham East GSP & Rochdale GSP | Private | Penwortham East GSP | Ribble 1 | 0.16738 | 0.43156 | 0.39001 | 1.1388 | 0.18612 | 433.0127 | 537.9855 | 2.01
Padiham GSP | Padiham | Padiham GSP | Huncoat 1 | 0.20992 | 0.52555 | 0.5598 | 1.4101 | 0.55631 | 433.0127 | 537.9855 | 2.45
Padiham GSP | Padiham | Rochdale GSP | Todmorden Tee 1 | 1.2978 | 3.3454 | 2.884 | 7.7291 | 0.7152 | 433.0127 | 537.9855 | 14.42
Padiham GSP | Padiham | Rochdale GSP | Todmorden Tee 2 | 1.2996 | 3.349 | 2.8989 | 7.7341 | 0.74366 | 433.0127 | 537.9855 | 14.46
Padiham GSP | Padiham | Padiham GSP | Rossendale 2 | 1.1574 | 2.9513 | 2.8031 | 7.9543 | 0.80269 | 534.9675 | 579.9746 | 12.98
Rochdale GSP | Scout Moor Tee | Rochdale GSP | ROCHDALE GSP | 0.27891 | 0.7127 | 0.69207 | 1.6372 | 0.7293 | 433.0127 | 537.9855 | 3.27
South Manchester GSP | South Manchester GSP | South Manchester GSP | West Didsbury 1 | 0.23849 | 0.17372 | 1.2289 | 0.43131 | 3.6937 | 337.0064 | 337.0064 | 2.565
0
0