## Disclaimer
Disclaimer
The information in this table should be read in conjunction with the explanatory notes in the main text.
The information contained in this statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval by Electricity North West, and payment of appropriate charges.
The information contained in this statement is the Copyright of Electricity North West, All Rights Reserved.

## 33kV TX Data Nov2024
TRANSFORMER DATA FOR 33kV PRIMARY SUBSTATIONS | [7 empty] | 8.43
BSP or S/S Group | Substation or busbar name |  |  |  |  | Vector Group | Positive Sequence Impedance |  | Zero Sequence Reactance | Tap |  | Transformer Rating | Reverse Power Capability | Method of Earthing
| Node 1 | System number | Voltage (kV) | Node 2 | Voltage (kV) |  | % on 100 MVA base |  | Xo | Maximum % | Minimum % | MVA | MVA | LV Earthing Impedance (Ohms)
[7 empty] | R | X
Adswood | BRINKSWAY | T11 | 33 | BRINKSWAY | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.4 | 11.5 / 23 | 10.6 / 10.59 | 3.81
Adswood | BRINKSWAY | T12 | 33 | BRINKSWAY | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.4 | 11.5 / 23 | 10.6 / 10.59 | 3.81
Adswood | CHEADLE HEATH | T11 | 33 | CHEADLE HEATH | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Adswood | CHEADLE HEATH | T12 | 33 | CHEADLE HEATH | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Adswood | CHEADLE HULME | T11 | 33 | CHEADLE HULME | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Adswood | CHEADLE HULME | T12 | 33 | CHEADLE HULME | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Adswood | WINIFRED RD | T11 | 33 | WINIFRED RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Adswood | WINIFRED RD | T12 | 33 | WINIFRED RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Agecroft | CHEETHAM HILL | T11 | 33 | CHEETHAM HILL | 6.6 | Dy11 | 3.97 | 116.52 | 99.04 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Agecroft | CHEETHAM HILL | T12 | 33 | CHEETHAM HILL | 6.6 | Dy11 | 4 | 114 | 97 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Agecroft | CLIFTON JUNCTION | T11 | 33 | CLIFTON JUNCTION | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Agecroft | MOSS LN | T12 | 33 | MOSS LN | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Agecroft | PRESTWICH | T11 | 33 | PRESTWICH | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Agecroft | PRESTWICH | T12 | 33 | PRESTWICH | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Agecroft | SWINTON | T11 | 33 | SWINTON | 11 | Yy0 | 4 | 100 | 333 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Agecroft | SWINTON | T12 | 33 | SWINTON | 11 | Yy0 | 4 | 100 | 333 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Agecroft | THE HEIGHT | T11 | 33 | THE HEIGHT | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.82
Agecroft | THE HEIGHT | T12 | 33 | THE HEIGHT | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.82
Altrincham | BOWDON | T11 | 33 | BOWDON | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.3
Altrincham | BOWDON | T12 | 33 | BOWDON | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.3
Altrincham | BROADHEATH | T11 | 33 | BROADHEATH | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 6.3
Altrincham | BROADHEATH | T12 | 33 | BROADHEATH | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 15 | Not Known | 9.4
Altrincham | BROADHEATH | T13 | 33 | BROADHEATH | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 6.3
Altrincham | GREEN LANE | T11 | 33 | GREEN LANE | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Altrincham | GREEN LANE | T12 | 33 | GREEN LANE | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Altrincham | MEDIPARK | T11 | 33 | MEDIPARK | 11 | Dx11 | 3.2 | 83.2 | 74.9 | 5.72 | -17.16 | 16 / 32 | Full Capability | 6.35
Atherton | ATHERTON TOWN CENTRE | T11 | 33 | ATHERTON TOWN CENTRE | 11 | Yy0 | 3 | 70 | 210 | 4.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Atherton | ATHERTON TOWN CENTRE | T12 | 33 | ATHERTON TOWN CENTRE | 11 | Yy0 | 3 | 70 | 210 | 4.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Atherton | BEDFORD | T11 | 33 | BEDFORD | 11 | Yy0 | 4 | 100 | 298.5 | 5.7 | -17.1 | 11.5 / 23 | 5.06 | 6.35
Atherton | BEDFORD | T12 | 33 | BEDFORD | 11 | Yy0 | 4 | 100 | 333 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Atherton | HINDLEY GREEN | T11 | 33 | HINDLEY GREEN | 11 | Dz0 | 4 | 104 | 306 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Atherton | HINDLEY GREEN | T12 | 33 | HINDLEY GREEN | 11 | Dz0 | 4 | 104 | 306 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Atherton | HINDLEY GREEN | T13 | 33 | HINDLEY GREEN | 11 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Atherton | KIRKHALL LANE | T11 | 33 | KIRKHALL LANE | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Atherton | KIRKHALL LANE | T12 | 33 | KIRKHALL LANE | 11 | Dz0 | 4 | 104 | 303 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Atherton | LEIGH | T11 | 33 | LEIGH | 11 | Yy0 | 8.86 | 115.2 | 870.9 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Barrow | BARROW GRID | T11 | 33 | BARROW | 11 | Dy11 | 4 | 104 | 88.4 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Barrow | BARROW GRID | T12 | 33 | BARROW | 11 | Dy11 | 5.3051 | 113.22 | 96.237 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Barrow | BOWATERS | T11 | 33 | BOWATERS | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Barrow | BOWATERS | T12 | 33 | BOWATERS | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Barrow | BOWATERS | T13 | 33 | BOWATERS | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Barrow | CHATSWORTH STREET | T11 | 33 | CHATSWORTH STREET | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Barrow | CHATSWORTH STREET | T12 | 33 | CHATSWORTH STREET | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Barton | BARTON DOCK RD | T11 | 33 | BARTON DOCK RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 12.5 | Not Known | 3.81
Barton | BARTON DOCK RD | T12 | 33 | BARTON DOCK RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 12.5 | Not Known | 3.81
Barton | CHASSEN RD | T11 | 33 | CHASSEN RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.82
Barton | CHASSEN RD | T12 | 33 | CHASSEN RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.82
Barton | DUMPLINGTON | T11 | 33 | DUMPLINGTON | 11 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Barton | DUMPLINGTON | T13 | 33 | DUMPLINGTON | 11 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Barton | LYONS RD | T11 | 33 | LYONS RD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Barton | LYONS RD | T12 | 33 | LYONS RD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Barton | MONTON | T11 | 33 | MONTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Barton | MONTON | T12 | 33 | MONTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Barton | MOUNT ST | T11 | 33 | MOUNT ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Barton | MOUNT ST | T12 | 33 | MOUNT ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Barton | TRAFFORD PARK NORTH | T11 | 33 | TRAFFORD PARK NORTH | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Barton | TRAFFORD PARK NORTH | T12 | 33 | TRAFFORD PARK NORTH | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Belfield | GALE | T11 | 33 | GALE | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 4.35
Belfield | GALE | T12 | 33 | GALE | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 4.35
Belfield | KINGSWAY | T11 | 33 | KINGSWAY | 11 | Dy11 | 4 | 79 | 67.15 | 5.7 | -17.2 | 19 / 38 | Full Capability | 6.35
Belfield | KINGSWAY | T12 | 33 | KINGSWAY | 11 | Dy11 | 4 | 79 | 67.15 | 5.7 | -17.2 | 19 / 38 | Full Capability | 6.35
Belfield | LITTLEBOROUGH | T11 | 33 | LITTLEBOROUGH | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Belfield | LITTLEBOROUGH | T12 | 33 | LITTLEBOROUGH | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Belfield | MILNROW | T11 | 33 | MILNROW | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Belfield | WARDLEWORTH | T11 | 33 | WARDLEWORTH | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Belfield | WARDLEWORTH | T12 | 33 | WARDLEWORTH | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Bispham | BISPHAM | T11 | 33 | BISPHAM | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bispham | BISPHAM | T12 | 33 | BISPHAM | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bispham | CLEVELEYS | T11 | 33 | CLEVELEYS | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Bispham | CLEVELEYS | T12 | 33 | CLEVELEYS | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Bispham | NORBRECK | T11 | 33 | NORBRECK | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Bispham | NORBRECK | T12 | 33 | NORBRECK | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Bispham | POULTON | T11 | 33 | POULTON | 6.6 | Dy11 | 4 | 101 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bispham | POULTON | T12 | 33 | POULTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bispham | WARBRECK | T11 | 33 | WARBRECK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Bispham | WARBRECK | T12 | 33 | WARBRECK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Blackburn | BLACKBURN | T11 | 33 | BLACKBURN | 6.6 | Dy11 | 4.4 | 87 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Blackburn | BLACKBURN | T12 | 33 | BLACKBURN | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Blackburn | CLARENDON RD | T11 | 33 | CLARENDON RD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackburn | CLARENDON RD | T12 | 33 | CLARENDON RD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackburn | PRINGLE ST | T11 | 33 | PRINGLE ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackburn | PRINGLE ST | T12 | 33 | PRINGLE ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackburn | RANDAL ST | T11 | 33 | RANDAL ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Blackburn | RANDAL ST | T12 | 33 | RANDAL ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Blackpool | BLACKPOOL | T11 | 33 | BLACKPOOL | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Blackpool | BLACKPOOL | T12 | 33 | BLACKPOOL | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 16 / 32 | Full Capability | 3.81
Blackpool | CECIL ST | T11 | 33 | CECIL ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Blackpool | CECIL ST | T12 | 33 | CECIL ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Blackpool | MARTON | T11 | 33 | MARTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Blackpool | MARTON | T12 | 33 | MARTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Blackpool | PRESTON OLD RD | T11 | 33 | PRESTON OLD RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Blackpool | PRESTON OLD RD | T12 | 33 | PRESTON OLD RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Blackpool | SHANNON ST | T13 | 33 | SHANNON ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackpool | SHANNON ST | T14 | 33 | SHANNON ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Blackpool | SQUIRES GATE | T11 | 33 | SQUIRES GATE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Blackpool | SQUIRES GATE | T12 | 33 | SQUIRES GATE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bloom Street | BRIDGEWATER | T11 | 33 | BRIDGEWATER | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bloom Street | BRIDGEWATER | T12 | 33 | BRIDGEWATER | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bloom Street | DEANSGATE | T11 | 33 | DEANSGATE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Bloom Street | DEANSGATE | T12 | 33 | DEANSGATE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Bloom Street | DICKINSON ST PRIMARY | T11 | 33 | DICKINSON ST PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 15 / 21 | Not Known | 3.81
Bloom Street | DICKINSON ST PRIMARY | T12 | 33 | DICKINSON ST PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Bloom Street | DICKINSON ST PRIMARY | T13 | 33 | DICKINSON ST PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 15 / 21 | Not Known | 3.81
Bloom Street | KNOTT MILL | T11 | 33 | KNOTT MILL | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Bloom Street | KNOTT MILL | T12 | 33 | KNOTT MILL | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Bloom Street | PICCADILLY | T11 | 33 | PICCADILLY | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | 14.54 | 3.81
Bloom Street | PICCADILLY | T12 | 33 | PICCADILLY | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | 14.54 | 3.81
Bolton | BARBARA ST | T11 | 33 | BARBARA ST | 6.6 | Ydy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 15 | Not Known | 3.81
Bolton | BARBARA ST | T12 | 33 | BARBARA ST | 6.6 | Ydy0 | 4 | 104 | 313 | 4.5 | -15 | 10 / 15 | Not Known | 3.81
Bolton | BRADSHAWGATE | T11 | 33 | BRADSHAWGATE | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Bolton | BRADSHAWGATE | T12 | 33 | BRADSHAWGATE | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Bolton | COX GREEN | T11 | 33 | COX GREEN | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Bolton | COX GREEN | T12 | 33 | COX GREEN | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Bolton | HARWOOD | T11 | 33 | HARWOOD | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Bolton | HARWOOD | T12 | 33 | HARWOOD | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Bolton | MUSGRAVE RD | T11 | 33 | MUSGRAVE RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bolton | MUSGRAVE RD | T12 | 33 | MUSGRAVE RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bolton | SPA RD | T11 | 33 | SPA RD | 6.6 | Dz0 | 4 | 100 | 300 | 4.5 | -15 | 15 / 21 | Not Known | 3.81
Bolton | SPA RD | T12 | 33 | SPA RD | 6.6 | Dz0 | 4 | 100 | 300 | 4.5 | -15 | 15 / 21 | Not Known | 3.81
Bolton | SPA RD | T13 | 33 | SPA RD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Bolton | UNION RD | T11 | 33 | UNION RD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Bolton | UNION RD | T12 | 33 | UNION RD | 6.6 | Yy0 | 4 | 100 | 300 | 6 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Bolton | WORDSWORTH ST | T11 | 33 | WORDSWORTH ST | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bolton | WORDSWORTH ST | T12 | 33 | WORDSWORTH ST | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Burnley | ATHLETIC ST | T11 | 33 | ATHLETIC ST | 6.6 | Ydy0 | 4 | 104 | 313 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Burnley | ATHLETIC ST | T12 | 33 | ATHLETIC ST | 6.6 | Ydy0 | 4 | 104 | 313 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Burnley | BURNLEY CENTRE | T11 | 33 | BURNLEY CENTRE | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Burnley | BURNLEY CENTRE | T12 | 33 | BURNLEY CENTRE | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Burnley | BURNLEY GSP | T11 | 33 | BURNLEY GSP | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 8.25 | 3.81
Burnley | BURNLEY GSP | T12 | 33 | BURNLEY GSP | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 8.25 | 3.81
Burnley | BURNLEY NORTH | T11 | 33 | BURNLEY NORTH | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Not Known | 4.35
Burnley | HEASANDFORD | T11 | 33 | HEASANDFORD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Burnley | HEASANDFORD | T12 | 33 | HEASANDFORD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bury | BURY TOWN CTR | T11 | 33 | BURY TOWN CENTRE | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bury | BURY TOWN CTR | T12 | 33 | BURY TOWN CENTRE | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Bury | CHAMBERHALL | T11 | 33 | CHAMBERHALL | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Bury | CHAMBERHALL | T12 | 33 | CHAMBERHALL | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Bury | DUMERS LANE | T11 | 33 | DUMERS LANE | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Bury | DUMERS LANE | T12 | 33 | DUMERS LANE | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Bury | HEAP BRIDGE | T11 | 33 | HEAP BRIDGE | 6.6 | Dz0 | 4 | 104 | 303 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Bury | HEAP BRIDGE | T12 | 33 | HEAP BRIDGE | 6.6 | Dz0 | 4 | 104 | 303 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Bury | HOLT ST | T11 | 33 | HOLT ST | 11 | Dz0 | 4 | 104 | 300 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Bury | HOLT ST | T12 | 33 | HOLT ST | 11 | Dz0 | 4 | 104 | 300 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Bury | WOOLFOLD | T11 | 33 | WOOLFOLD | 11 | Yy0 | 4 | 104 | 100 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Bury | WOOLFOLD | T12 | 33 | WOOLFOLD | 11 | Yy0 | 4 | 104 | 100 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Buxton | ASHWOOD DALE | T11 | 33 | ASHWOOD DALE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Buxton | ASHWOOD DALE | T12 | 33 | ASHWOOD DALE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Buxton | FERODO | T11 | 33 | FERODO | 11 | Dy11 | 4 | 100 | 85 | 5.6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Buxton | WATERSWALLOWS | T11 | 33 | WATERSWALLOWS | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Buxton | WATERSWALLOWS | T12 | 33 | WATERSWALLOWS | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | CAPONTREE | T11 | 33 | CAPONTREE | 11 | Dy11 | 4.5 | 113.56 | 96.526 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | solid
Carlisle | CAPONTREE | T12 | 33 | CAPONTREE | 11 | Dy11 | 5 | 113.56 | 96.526 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | solid
Carlisle | FUSEHILL | T11 | 33 | FUSEHILL | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Carlisle | FUSEHILL | T12 | 33 | FUSEHILL | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Carlisle | JAMES ST | T11 | 33 | JAMES ST | 11 | Dy11 | 4 | 100 | 85 | 6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | JAMES ST | T12 | 33 | JAMES ST | 11 | Dy11 | 4 | 100 | 85 | 6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | MORTON PK | T11 | 33 | MORTON PK | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | MORTON PK | T12 | 33 | MORTON PK | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | PETTERIL BANK | T11 | 33 | PETTERIL BANK | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Carlisle | PETTERIL BANK | T12 | 33 | PETTERIL BANK | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Carlisle | PIRELLI | T12 | 33 | PIRELLI | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -19.5 | 7.5 / 13.5 | Not Known | 6.35
Carlisle | SEBERGHAM | T11 | 33 | SEBERGHAM | 11 | Dx11 | 11.79 | 150.38 | 127.823 | 5.7 | -17.2 | 4 / 8 | Full Capability | solid
Carlisle | SILLOTH | T11 | 33 | SILLOTH | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | SILLOTH | T12 | 33 | SILLOTH | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | SILLOTH | T13 | 33 | SILLOTH | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Carlisle | WESTLINTON | T11 | 33 | WESTLINTON | 11 | Dx11 | 8.645 | 113.538 | 96.5073 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Carlisle | WESTLINTON | T12 | 33 | WESTLINTON | 11 | Dx11 | 8.714 | 116.54 | 99.059 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Carlisle | WIGTON | T11 | 33 | WIGTON | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | WIGTON | T12 | 33 | WIGTON | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carlisle | WILLOWHOLME | T11 | 33 | WILLOWHOLME | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Carlisle | WILLOWHOLME | T12 | 33 | WILLOWHOLME | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Carrington | IRLAM PRIMARY | T11 | 33 | IRLAM PRIMARY | 6.6 | Dy11 | 5.2347 | 114.565 | 114.565 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Carrington | IRLAM PRIMARY | T12 | 33 | IRLAM PRIMARY | 6.6 | Dy11 | 5.2347 | 114.565 | 114.565 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Carrington | NWGB PARTINGTON | T11 | 33 | NWGB PARTINGTON | 6.6 | Yd11 | 4 | 104 | 85 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Carrington | NWGB PARTINGTON | T12 | 33 | NWGB PARTINGTON | 6.6 | Yd11 | 4 | 104 | 85 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Castleton | CASTLETON PRIMARY | T11 | 33 | CASTLETON PRIMARY | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Castleton | CASTLETON PRIMARY | T12 | 33 | CASTLETON PRIMARY | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Not Known | 3.81
Castleton | HEADY HILL | T11 | 33 | HEADY HILL | 6.6 | Ydy0 | 4 | 104 | 291 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Castleton | HEADY HILL | T12 | 33 | HEADY HILL | 6.6 | Ydy0 | 4 | 104 | 291 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Castleton | HEYWOOD | T11 | 33 | HEYWOOD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Castleton | HEYWOOD | T12 | 33 | HEYWOOD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Castleton | MILNROW | T12 | 33 | MILNROW | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Castleton | WOODBINE ST | T11 | 33 | WOODBINE ST | 6.6 | Yy0 | 4 | 104 | 309 | 4.5 | -15 | 10 / 14 | Not Known | 4.35
Castleton | WOODBINE ST | T12 | 33 | WOODBINE ST | 6.6 | Yy0 | 4 | 104 | 306 | 4.5 | -15 | 10 / 14 | Not Known | 4.35
Chadderton | CHADDERTON PRIMARY | T11 | 33 | CHADDERTON PRIMARY | 6.6 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.1 | 19 / 38 | 8.69 | 3.81
Chadderton | CHADDERTON PRIMARY | T12 | 33 | CHADDERTON PRIMARY | 6.6 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.1 | 19 / 38 | 8.69 | 3.81
Chadderton | FAILSWORTH | T11 | 33 | FAILSWORTH | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Chadderton | FAILSWORTH | T12 | 33 | FAILSWORTH | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Chadderton | HOLLINWOOD | T11 | 33 | HOLLINWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Chadderton | HOLLINWOOD | T12 | 33 | HOLLINWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Chadderton | LANGLEY | T11 | 33 | LANGLEY | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 6.35
Chadderton | LANGLEY | T12 | 33 | LANGLEY | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 6.35
Chadderton | MIDDLETON JUNCTION | T11 | 33 | MIDDLETON JUNCTION | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 6.35
Chadderton | MIDDLETON JUNCTION | T12 | 33 | MIDDLETON JUNCTION | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 6.35
Chadderton | NEW MOSTON | T11 | 33 | NEW MOSTON | 6.6 | Dy11 | 3.857 | 117 | 99.45 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Chadderton | NEW MOSTON | T12 | 33 | NEW MOSTON | 6.6 | Dy11 | 3.857 | 117 | 99.45 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Chadderton | NEWTON HEATH | T11 | 33 | NEWTON HEATH | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 | Not Known | 3.81
Chadderton | TOWNLEY ST | T11 | 33 | TOWNLEY ST | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -18 | 15 / 21 | Full Capability | 6.35
Chadderton | TOWNLEY ST | T12 | 33 | TOWNLEY ST | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -18 | 15 / 21 | Full Capability | 6.35
Droylsden | DENTON EAST | T11 | 33 | DENTON EAST | 6.6 | Dy11 | 3.89 | 117.2 | 99.62 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Droylsden | DENTON EAST | T12 | 33 | DENTON EAST | 6.6 | Dy11 | 3.88 | 114.98 | 97.733 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.54
Droylsden | DENTON WEST | T11 | 33 | DENTON WEST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Droylsden | DENTON WEST | T12 | 33 | DENTON WEST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Droylsden | DROYLSDEN | T11 | 33 | SNIPE | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Droylsden | DROYLSDEN | T12 | 33 | SNIPE | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Droylsden | DROYLSDEN EAST | T11 | 33 | DROYLSDEN EAST | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Droylsden | DROYLSDEN EAST | T12 | 33 | DROYLSDEN EAST | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Droylsden | OPENSHAW | T11 | 33 | OPENSHAW | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Droylsden | OPENSHAW | T12 | 33 | OPENSHAW | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Egremont | CARLETON | T11 | 33 | CARLETON | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | solid
Egremont | EGREMONT PRIMARY | T11 | 33 | EGREMONT PRIMARY | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | 7.5 / 10.5 | 6.35
Egremont | EGREMONT PRIMARY | T12 | 33 | EGREMONT PRIMARY | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | 7.5 / 10.5 | 6.35
Egremont | HENSINGHAM | T11 | 33 | HENSINGHAM | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Egremont | HENSINGHAM | T12 | 33 | HENSINGHAM | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Egremont | MIDWAY | T11 | 33 | MIDWAY | 11 | Dy11 | 5 | 133 | 113.05 | 17.2 | -5.7 | 7.5 / 15 | 7.5 / 10.51 | solid
Egremont | MIDWAY | T12 | 33 | MIDWAY | 11 | Dy11 | 5 | 133 | 113.05 | 17.2 | -5.7 | 7.5 / 15 | 7.5 / 10.51 | solid
Egremont | SLIPWAY | T11 | 33 | SLIPWAY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 | Full Capability | 6.35
Egremont | SLIPWAY | T12 | 33 | SLIPWAY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 | Full Capability | 6.35
Frederick Road | BLACKFRIARS | T11 | 33 | BLACKFRIARS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | BLACKFRIARS | T12 | 33 | BLACKFRIARS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | CHAPEL WHARF | T11 | 33 | CHAPEL WHARF | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | CHAPEL WHARF | T12 | 33 | CHAPEL WHARF | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | FREDERICK RD | T11 | 33 | FREDERICK RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | FREDERICK RD | T12 | 33 | FREDERICK RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | FREDERICK RD | T11 | 33 | ST JOHNS | 6.6 | Dy11 | 3.971 | 114.478 | 97.3063 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | FREDERICK RD | T12 | 33 | ST JOHNS | 6.6 | Dy11 | 3.893 | 114.826 | 97.6021 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | PENDLETON | T11 | 33 | PENDLETON | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Frederick Road | PENDLETON | T12 | 33 | PENDLETON | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Frederick Road | ROBERT HALL ST | T11 | 33 | ROBERT HALL ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Frederick Road | ROBERT HALL ST | T12 | 33 | ROBERT HALL ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Frederick Road | SALFORD QUAYS | T11 | 33 | SALFORD QUAYS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | SALFORD QUAYS | T12 | 33 | SALFORD QUAYS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | TRINITY | T11 | 33 | TRINITY | 6.6 | Dy11 | 4.5 | 114 | 97 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Frederick Road | TRINITY | T12 | 33 | TRINITY | 6.6 | Dy11 | 4.5 | 115 | 97.8 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Frederick Road | TRINITY | T13 | 33 | TRINITY | 6.6 | Dy11 | 3.904 | 116.478 | 99.006 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Frederick Road | WEASTE PRY | T11 | 33 | WEASTE PRY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Frederick Road | WEASTE PRY | T12 | 33 | WEASTE PRY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Golborne | ASHTON | T11 | 33 | ASHTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Golborne | ASHTON | T12 | 33 | ASHTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Golborne | CULCHETH | T12 | 33 | CULCHETH | 11 | Yy0 | 5 | 112 | 337 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Golborne | GOLBORNE | T11 | 33 | GOLBORNE | 11 | Ydy0 | 4 | 104 | 511.7 | 4.5 | -15 | 16 / 32 | Full Capability | 6.35
Golborne | GOLBORNE | T12 | 33 | GOLBORNE | 11 | Ydy0 | 4 | 104 | 511.82 | 4.5 | -15 | 16 / 32 | Full Capability | 6.35
Golborne | GOLBORNE | T13 | 33 | GOLBORNE | 11 | Ydy0 | 4.13 | 112 | 771.9 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Golborne | HAYDOCK PRY | T11 | 33 | HAYDOCK PRY | 11 | Ydy0 | 4 | 85 | 244.5 | 5.72 | -17.16 | 16 / 32 | Full Capability | 6.35
Golborne | HAYDOCK PRY | T12 | 33 | HAYDOCK PRY | 11 | Ydy0 | 4 | 85 | 244.5 | 5.72 | -17.16 | 16 / 32 | Full Capability | 6.35
Golborne | NEWTON LE WILLOWS | T11 | 33 | NEWTON LE WILLOWS | 11 | Yy0 | 4.15 | 115.26 | 755 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Golborne | NEWTON LE WILLOWS | T12 | 33 | NEWTON LE WILLOWS | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 6.35
Golborne | RISLEY | T11 | 33 | RISLEY | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Greenhill | BELGRAVE | T11 | 33 | BELGRAVE | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Greenhill | BELGRAVE | T12 | 33 | BELGRAVE | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Greenhill | GREENHILL | T11 | 33 | GREENHILL | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Greenhill | GREENHILL | T12 | 33 | GREENHILL | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Greenhill | GREENHILL | T13 | 33 | GREENHILL | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Greenhill | ST MARYS | T11 | 33 | ST MARYS | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.3 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Greenhill | ST MARYS | T12 | 33 | ST MARYS | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.3 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Greenhill | WATERHEAD | T11 | 33 | WATERHEAD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Greenhill | WATERHEAD | T12 | 33 | WATERHEAD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Greenhill | WERNETH | T11 | 33 | WERNETH | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Greenhill | WERNETH | T12 | 33 | WERNETH | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Hazel Grove | BRAMHALL | T11 | 33 | BRAMHALL | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Hazel Grove | BRAMHALL | T12 | 33 | BRAMHALL | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Hazel Grove | DISLEY | T12 | 33 | DISLEY | 11 | Dy11 | 4 | 100 | 85 | 4 | -12 | 11.5 / 23 | Full Capability | 6.35
Hazel Grove | GREEN LANE | T11 | 33 | GREEN LANE | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Hazel Grove | GREEN LANE | T12 | 33 | GREEN LANE | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Hazel Grove | HAWK GREEN | T11 | 33 | HAWK GREEN | 11 | Dy11 | 3.722 | 114.348 | 113.502 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Hazel Grove | HAWK GREEN | T12 | 33 | HAWK GREEN | 11 | Dy11 | 3.8043 | 114.913 | 114.063 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Hazel Grove | MARPLE | T11 | 33 | MARPLE | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 5 | Full Capability | 6.35
Hazel Grove | NORBURY | T11 | 33 | NORBURY | 11 | Dy11 | 4 | 100 | 85 | 4.2 | -18.5 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Hazel Grove | NORBURY | T12 | 33 | NORBURY | 11 | Dy11 | 4 | 100 | 85 | 4.2 | -18.5 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Vernon Park | OFFERTON | T11 | 33 | OFFERTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Vernon Park | OFFERTON | T12 | 33 | OFFERTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Hazel Grove | POYNTON | T11 | 33 | POYNTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Hazel Grove | POYNTON | T12 | 33 | POYNTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Heyrod | ASHTON UNDER LYNE | T11 | 33 | ASHTON UNDER LYNE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 5.72
Heyrod | ASHTON UNDER LYNE | T12 | 33 | ASHTON UNDER LYNE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 5.72
Heyrod | ASHTON UNDER LYNE | T13 | 33 | ASHTON UNDER LYNE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 5.72
Heyrod | GLOSSOP | T12 | 33 | GLOSSOP | 11 | Dy11 | 5.2 | 114 | 96.9 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Heyrod | GREENFIELD | T11 | 33 | GREENFIELD | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Heyrod | GREENFIELD | T12 | 33 | GREENFIELD | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Heyrod | HEYROD PRIMARY | T11 | 33 | HEYROD PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Heyrod | HEYROD PRIMARY | T12 | 33 | HEYROD PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Heyrod | HURST | T11 | 33 | HURST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Heyrod | HURST | T12 | 33 | HURST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Heyrod | MOSSLEY | T11 | 33 | MOSSLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Heyrod | MOSSLEY | T12 | 33 | MOSSLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Heyrod | TAME VALLEY | T11 | 33 | TAME VALLEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Heyrod | TAME VALLEY | T12 | 33 | TAME VALLEY | 6.6 | Dy11 | 3.8956 | 117.348 | 99.7458 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Huncoat | CLAYTON | T11 | 33 | CLAYTON | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Huncoat | CLAYTON | T12 | 33 | CLAYTON | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Huncoat | CHURCH | T11 | 33 | CHURCH | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Huncoat | COG LANE | T11 | 33 | COG LANE | 6.6 | Yy0 | 4 | 85 | 255 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Huncoat | COG LANE | T12 | 33 | COG LANE | 6.6 | Yy0 | 4 | 85 | 255 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Huncoat | GREAT HARWOOD | T11 | 33 | GREAT HARWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Huncoat | GREAT HARWOOD | T12 | 33 | GREAT HARWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Huncoat | HYNDBURN RD | T11 | 33 | HYNDBURN RD | 6.6 | Yy0 | 4 | 100 | 312 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Huncoat | HYNDBURN RD | T12 | 33 | HYNDBURN RD | 6.6 | Yy0 | 4.416 | 112.087 | 312 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Huncoat | KAY ST | T11 | 33 | KAY ST | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Huncoat | KAY ST | T12 | 33 | KAY ST | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Huncoat | STRAWBERRY BANK | T11 | 33 | STRAWBERRY BANK | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Huncoat | STRAWBERRY BANK | T12 | 33 | STRAWBERRY BANK | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Hyde | DUKINFIELD | T11 | 33 | DUKINFIELD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Hyde | DUKINFIELD | T12 | 33 | DUKINFIELD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Hyde | GLOSSOP | T11 | 33 | GLOSSOP | 11 | Dy11 | 5.2 | 114 | 96.9 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Hyde | HADFIELD | T11 | 33 | HADFIELD | 11 | Dy11 | 4 | 100 | 85 | 4.4 | -18.6 | 11.5 / 23 | Not Known | 6.35
Hyde | HADFIELD | T12 | 33 | HADFIELD | 11 | Dy11 | 4 | 100 | 85 | 4.4 | -18.6 | 11.5 / 23 | Not Known | 6.35
Hyde | HATTERSLEY | T11 | 33 | HATTERSLEY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Hyde | HATTERSLEY | T12 | 33 | HATTERSLEY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Hyde | HYDE PRIMARY | T11 | 33 | HYDE PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Hyde | HYDE PRIMARY | T12 | 33 | HYDE PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Hyde | NEWTON | T11 | 33 | NEWTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 12.5 | Not Known | 6.35
Hyde | NEWTON | T12 | 33 | NEWTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 12.5 | Not Known | 6.35
Kearsley Local | CAMPBELL ST | T11 | 33 | CAMPBELL ST | 11 | Yy0 | 4 | 112 | 756 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | CAMPBELL ST | T12 | 33 | CAMPBELL ST | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Kearsley Local | CARR ST | T11 | 33 | CARR ST | 11 | Yy0 | 4 | 100 | 664.4 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | CARR ST | T12 | 33 | CARR ST | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Kearsley Local | CLIFTON JUNCTION | T12 | 33 | CLIFTON JUNCTION | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Kearsley Local | CUTACRE | T11 | 33 | CUTACRE | 11 | Yy0 | 4.209 | 110.96 | 764.5 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | CUTACRE | T12 | 33 | CUTACRE | 11 | Yy0 | 4.191 | 110.7 | 762.7 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | FARNWORTH | T11 | 33 | FARNWORTH | 11 | Yy0 | 4 | 100 | 333 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | FARNWORTH | T12 | 33 | FARNWORTH | 11 | Yy0 | 4 | 100 | 333 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | HILL TOP | T11 | 33 | HILL TOP | 11 | Yy0 | 4 | 100 | 288 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 10.6
Kearsley Local | HILL TOP | T12 | 33 | HILL TOP | 11 | Yy0 | 4 | 100 | 288 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 10.6
Kearsley Local | HILL TOP | T13 | 33 | HILL TOP | 11 | Ydy0 | 4 | 104 | 312 | 4.5 | -15 | 10 | Not Known | 10.6
Kearsley Local | LITTLE HULTON | T11 | 33 | LITTLE HULTON | 11 | Dz0 | 4 | 104 | 309 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Kearsley Local | LITTLE HULTON | T12 | 33 | LITTLE HULTON | 11 | Dz0 | 4 | 104 | 315 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Kearsley Local | MOSS LN | T11 | 33 | MOSS LN | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | RINGLEY | T11 | 33 | RINGLEY | 11 | Yy0 | 4.46 | 114.35 | 343.05 | 4.4 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Kearsley Local | RINGLEY | T12 | 33 | RINGLEY | 11 | Yy0 | 4.482 | 115.48 | 346.44 | 4.4 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Kendal | AMBLESIDE | T11 | 33 | AMBLESIDE | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -16.5 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Kendal | AMBLESIDE | T12 | 33 | AMBLESIDE | 11 | Dy11 | 4 | 100 | 85 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Kendal | ARNSIDE | T11 | 33 | ARNSIDE | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Kendal | ARNSIDE | T12 | 33 | ARNSIDE | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Kendal | BENTHAM | T11 | 33 | BENTHAM | 11 | Ydy0 | 5 | 133 | 1113 | 5.72 | -17.16 | 10 | Not Known | 6.35
Kendal | INGLETON | T11 | 33 | INGLETON | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | 6.91 | 6.35
Kendal | KENDAL GRID | T11 | 33 | KENDAL GRID | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Kendal | KENDAL GRID | T12 | 33 | KENDAL GRID | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Kendal | KIRKBY LONSDALE | T11 | 33 | KIRKBY LONSDALE | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 4 / 8 | Not Known | 6.35
Kendal | KIRKBY LONSDALE | T12 | 33 | KIRKBY LONSDALE | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 4 / 8 | Not Known | 6.35
Kendal | MELLING | T11 | 33 | MELLING | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 4 / 8 | Full Capability | 6.35
Kendal | MINTSFEET | T11 | 33 | MINTSFEET | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Kendal | MINTSFEET | T12 | 33 | MINTSFEET | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Kendal | ROAN EDGE | T11 | 33 | ROAN EDGE | LV | Dy11 | 10 | 510 | 433.5 | 5 | -5 | 1 | Not Known | solid
Kendal | SEDBERGH | T11 | 33 | SEDBERGH | 11 | Dy11 | 8.9755 | 115.7333 | 100.0632 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | solid
Kendal | SEDBERGH | T12 | 33 | SEDBERGH | 11 | Dy11 | 8.9755 | 115.7333 | 100.0632 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | solid
Kendal | WHASSET | T11 | 33 | WHASSET | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Kendal | WHASSET | T12 | 33 | WHASSET | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Kendal | WINDERMERE | T11 | 33 | WINDERMERE | 11 | Dy11 | 5.168 | 113.48 | 96.458 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Kendal | WINDERMERE | T12 | 33 | WINDERMERE | 11 | Dy11 | 4 | 104 | 88.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Kendal | YEALAND | T11 | 33 | YEALAND | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | Not Known | 6.35
Lancaster | BOLTON LE SANDS | T11 | 33 | BOLTON LE SANDS | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Lancaster | BOLTON LE SANDS | T12 | 33 | BOLTON LE SANDS | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Lancaster | BROADWAY | T11 | 33 | BROADWAY | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 3.81
Lancaster | BROADWAY | T12 | 33 | BROADWAY | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 3.81
Lancaster | BURROW BECK | T11 | 33 | BURROW BECK | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -16.5 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Lancaster | BURROW BECK | T12 | 33 | BURROW BECK | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -16.5 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Lancaster | CLAUGHTON | T11 | 33 | CLAUGHTON | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Lancaster | LANCASTER GRID | T11 | 33 | LANCASTER PRIMARY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Lancaster | LANCASTER GRID | T12 | 33 | LANCASTER PRIMARY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Lancaster | SPRING GARDEN STREET | T11 | 33 | SPRING GARDEN STREET | 6.6 | Yy0 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Lancaster | SPRING GARDEN STREET | T12 | 33 | SPRING GARDEN STREET | 6.6 | Yy0 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Lancaster | SPRING GARDEN STREET | T13 | 33 | SPRING GARDEN STREET | 11 | Dy11 | 4 | 81.5 | 69.275 | 4.5 | -15 | 16 / 32 | Full Capability | 6.35
Lancaster | SPRING GARDEN STREET | T14 | 33 | SPRING GARDEN STREET | 11 | Dy11 | 4 | 81.5 | 69.275 | 4.5 | -15 | 16 / 32 | Full Capability | 6.35
Lancaster | WESTGATE | T11 | 33 | WESTGATE | 6.6 | Dy11 | 5.3 | 114.22 | 97.09 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Lancaster | WESTGATE | T12 | 33 | WESTGATE | 6.6 | Dy11 | 5.267 | 114.261 | 112.599 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Lancaster | WOODHILL LANE | T11 | 33 | WOODHILL LANE | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Leyland | BOW LANE | T11 | 33 | BOW LANE | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Leyland | BOW LANE | T12 | 33 | BOW LANE | 11 | Yy0 | 4 | 100 | 300 | 5.72 | -17.16 | 11.5 / 23 | 5.06 | 6.35
Leyland | BUCKSHAW | T11 | 33 | BUCKSHAW | 11 | Yx0 | 5.1 | 115.22 | 345.66 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Leyland | BUCKSHAW | T12 | 33 | BUCKSHAW | 11 | Yx0 | 5.1 | 116 | 343.83 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Leyland | MOSS SIDE | T12 | 33 | MOSS SIDE | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Leyland | SEVEN STARS | T11 | 33 | SEVEN STARS | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | Full Capability | 6.35
Leyland | WHITTLE LE WOODS | T11 | 33 | WHITTLE LE WOODS | 11 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Leyland | WHITTLE LE WOODS | T12 | 33 | WHITTLE LE WOODS | 11 | Dz0 | 4 | 104 | 309 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Longsight | CIRCLE SQUARE | T11 | 33 | CIRCLE SQUARE | 6.6 | Dy11 | 4.07 | 112.217 | 95.384 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
West Didsbury | FALLOWFIELD | T11 | 33 | FALLOWFIELD | 6.6 | Dy11 | 4 | 100 | 85 | 5 | -5 | 11.5 / 23 | 11.5 / 13.11 | 3.81
West Didsbury | FALLOWFIELD | T12 | 33 | FALLOWFIELD | 6.6 | Dy11 | 5.28 | 117.2 | 99.62 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Longsight | LEVENSHULME | T11 | 33 | LEVENSHULME | 6.6 | Dx11 | 5.528 | 114.17 | 97.0445 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Longsight | LEVENSHULME | T12 | 33 | LEVENSHULME | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Longsight | LONGSIGHT PRIMARY | T11 | 33 | LONGSIGHT PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | LONGSIGHT PRIMARY | T12 | 33 | LONGSIGHT PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | MANCHESTER UNIVERSITY | T11 | 33 | MANCHESTER UNIVERSITY | 6.6 | Dy11 | 4 | 100 | 85 | 5.8 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | MANCHESTER UNIVERSITY | T12 | 33 | MANCHESTER UNIVERSITY | 6.6 | Dy11 | 4 | 100 | 85 | 5.8 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | MOSS SIDE | T11 | 33 | MOSS SIDE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | MOSS SIDE | T12 | 33 | MOSS SIDE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Longsight | VICTORIA PARK | T11 | 33 | VICTORA PARK | 6.6 | Dy11 | 5.28 | 117.2 | 99.62 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Longsight | VICTORIA PARK | T12 | 33 | VICTORA PARK | 6.6 | Dy11 | 5.27 | 117.2 | 99.62 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | ALBION ST | T11 | 33 | ALBION ST | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Lower Darwen | ALBION ST | T12 | 33 | ALBION ST | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Lower Darwen | EXCHANGE ST | T11 | 33 | EXCHANGE ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Lower Darwen | EXCHANGE ST | T12 | 33 | EXCHANGE ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Lower Darwen | FENISCOWLES | T11 | 33 | FENISCOWLES | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | FENISCOWLES | T12 | 33 | FENISCOWLES | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | GRIFFIN | T11 | 33 | GRIFFIN | 6.6 | Dy11 | 4 | 113 | 96.05 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | GRIFFIN | T12 | 33 | GRIFFIN | 6.6 | Dy11 | 4 | 113 | 96.05 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | INDIA ST | T11 | 33 | INDIA ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Lower Darwen | INDIA ST | T12 | 33 | INDIA ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.81
Lower Darwen | LOWER DARWEN PRIMARY | T11 | 33 | LOWER DARWEN PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Lower Darwen | LOWER DARWEN PRIMARY | T12 | 33 | LOWER DARWEN PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Lower Darwen | ROMAN RD | T11 | 33 | ROMAN RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Lower Darwen | ROMAN RD | T12 | 33 | ROMAN RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Lytham | ANSDELL | T11 | 33 | ANSDELL | 6.6 | Yy0 | 4 | 100 | 317 | 10.5 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Lytham | ANSDELL | T12 | 33 | ANSDELL | 6.6 | Yy0 | 4 | 100 | 300 | 10.5 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Lytham | SOUTH PARK | T11 | 33 | SOUTH PARK | 11 | Yy0 | 4 | 100 | 276 | 4.5 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Lytham | SOUTH PARK | T12 | 33 | SOUTH PARK | 11 | Yy0 | 4 | 100 | 276 | 4.5 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Lytham | ST ANNES | T11 | 33 | ST ANNES | 6.6 | Yy0 | 4 | 104 | 85 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Lytham | ST ANNES | T12 | 33 | ST ANNES | 6.6 | Yy0 | 4 | 104 | 306 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Lytham | ST THOMAS RD | T11 | 33 | ST THOMAS RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Lytham | ST THOMAS RD | T12 | 33 | ST THOMAS RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Macclesfield | BOLLINGTON | T11 | 33 | BOLLINGTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.3 | -15 | 10 | Full Capability | 6.35
Macclesfield | BOLLINGTON | T12 | 33 | BOLLINGTON | 11 | Dy11 | 4 | 104 | 88.4 | 4.3 | -15 | 10 | Not Known | 6.35
Macclesfield | S.E. MACCLESFIELD | T11 | 33 | S.E. MACCLESFIELD | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.4 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Macclesfield | S.E. MACCLESFIELD | T12 | 33 | S.E. MACCLESFIELD | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Macclesfield | S.W. MACCLESFIELD | T11 | 33 | S.W. MACCLESFIELD | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Macclesfield | S.W. MACCLESFIELD | T12 | 33 | S.W. MACCLESFIELD | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 6.35
Macclesfield | WITHYFOLD DRIVE | T11 | 33 | WITHYFOLD DRIVE | 11 | Dy11 | 4 | 104 | 88.4 | 4.3 | -15 | 10 / 14 | Not Known | 6.35
Macclesfield | WITHYFOLD DRIVE | T12 | 33 | WITHYFOLD DRIVE | 11 | Dy11 | 4.4 | 87 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Macclesfield | WITHYFOLD DRIVE | T13 | 33 | WITHYFOLD DRIVE | 11 | Dy11 | 4.4 | 87 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Moss Nook | ALDERLEY | T11 | 33 | ALDERLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Moss Nook | ALDERLEY | T12 | 33 | ALDERLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Moss Nook | CHELFORD | T11 | 33 | CHELFORD | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | 6.35
Moss Nook | GATLEY | T12 | 33 | GATLEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Moss Nook | HANDFORTH | T11 | 33 | HANDFORTH | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Moss Nook | HANDFORTH | T12 | 33 | HANDFORTH | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Moss Nook | HIGHER MILL | T11 | 33 | HIGHER MILL | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Moss Nook | HIGHER MILL | T12 | 33 | HIGHER MILL | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Moss Nook | MANCHESTER AIRPORT PLC | T11 | 33 | MANCHESTER AIRPORT PLC | 11 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.2 | 19 / 38 | Not Known | 6.35
Moss Nook | MANCHESTER AIRPORT PLC | T12 | 33 | MANCHESTER AIRPORT PLC | 11 | Dy11 | 3 | 70 | 59.5 | 5.7 | -17.2 | 19 / 38 | Not Known | 6.35
Moss Nook | MOSS NOOK | T11 | 33 | MOSS NOOK PRIMARY | 11 | Dx11 | 4 | 82.38 | 70.0192 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.351
Moss Nook | MOSS NOOK | T11 | 33 | THORLEY LANE | 11 | Dx11 | 3.069 | 81.625 | 69.381 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Moss Nook | MOSS NOOK | T12 | 33 | THORLEY LANE | 11 | Dx11 | 3.097 | 82.375 | 70.019 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Moss Nook | WILMSLOW | T11 | 33 | WILMSLOW | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Moss Nook | WILMSLOW | T12 | 33 | WILMSLOW | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Moss Nook | WOODHOUSE PARK | T11 | 33 | WOODHOUSE PARK | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 6.3
Moss Nook | WOODHOUSE PARK | T12 | 33 | WOODHOUSE PARK | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 6.3
Nelson | CLOVER HILL | T11 | 33 | CLOVER HILL | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Nelson | CLOVER HILL | T12 | 33 | CLOVER HILL | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Nelson | FLAT LANE | T11 | 33 | FLAT LANE | 11 | Dz0 | 4 | 104 | 88 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Nelson | HELWITH BRIDGE | T11 | 33 | HELWITH BRIDGE | 11 | Yy0 | 5 | 133 | 112 | 5.7 | -17.2 | 7.5 / 15 | 5.06 | 6.35
Nelson | LANGROYD RD | T11 | 33 | LANGROYD RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.5 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Nelson | LANGROYD RD | T12 | 33 | LANGROYD RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.5 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Nelson | NELSON PRIMARY | T11 | 33 | NELSON PRIMARY | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Nelson | NELSON PRIMARY | T12 | 33 | NELSON PRIMARY | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Nelson | PHILLIPS LANE | T11 | 33 | PHILLIPS LANE | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Nelson | SETTLE | T11 | 33 | SETTLE | 11 | Dz0 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Nelson | SPRING COTTAGE | T11 | 33 | SPRING COTTAGE | 6.6 | Ydy0 | 3.79 | 110 | 660 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Nelson | SPRING COTTAGE | T12 | 33 | SPRING COTTAGE | 6.6 | Ydy0 | 3.978 | 110.78 | 664.68 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
New Mills | FERODO | T12 | 33 | FERODO | 11 | Dy11 | 4 | 100 | 85 | 5.6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
New Mills | GOWHOLE | T11 | 33 | GOWHOLE | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 6.35
New Mills | GOWHOLE | T12 | 33 | GOWHOLE | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 6.35
Padiham | BOLTON BY BOWLAND | T11 | 33 | BOLTON BY BOWLAND | 11 | Yy0 | 5 | 133 | 401 | 12 | -10 | 7.5 | Full Capability | 6.35
Padiham | PADIHAM | T11 | 33 | PADIHAM | 11 | Yy0 | 3 | 70 | 216 | 4.3 | -18.6 | 19 / 38 | 8.42 | 6.32
Padiham | PADIHAM | T12 | 33 | PADIHAM | 11 | Yy0 | 3 | 70 | 216 | 4.3 | -18.6 | 19 / 38 | 8.42 | 6.32
Padiham | PEEL ST | T11 | 33 | PEEL ST | 11 | Ydy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Padiham | RIBBLESDALE | T13 | 33 | RIBBLESDALE | 11 | Ydy0 | 4 | 104 | 300 | 4.5 | -15 | 10 / 12.5 | Not Known | 6.35
Padiham | RIBBLESDALE | T14 | 33 | RIBBLESDALE | 11 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Padiham | WHALLEY | T11 | 33 | WHALLEY | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.32
Padiham | WHALLEY | T12 | 33 | WHALLEY | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.32
Peel | HALL CROSS | T11 | 33 | HALL CROSS | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Peel | HALL CROSS | T12 | 33 | HALL CROSS | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Peel | MERESIDE | T11 | 33 | MERESIDE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Peel | MERESIDE | T12 | 33 | MERESIDE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Peel | WARTON | T11 | 33 | WARTON | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Peel | WARTON | T12 | 33 | WARTON | 6.6 | Yy0 | 3.9 | 111 | 666 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Penrith/Shap | ALSTON | T11 | 33 | ALSTON | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -10.5 | 3 | Not Known | solid
Penrith/Shap | GILLSROW | T11 | 33 | GILLSROW | 11 | Dy11 | 8.758 | 113.67 | 96.6195 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Penrith/Shap | HUTTON END | T11 | 33 | HUTTON END | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Penrith/Shap | HUTTON END | T12 | 33 | HUTTON END | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Penrith/Shap | KESWICK | T12 | 33 | KESWICK | 11 | Dy11 | 8.81 | 115.7 | 113 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Penrith/Shap | KIRKBY STEPHEN | T11 | 33 | KIRKBY STEPHEN | 11 | Dy11 | 9.5414 | 113.067 | 113.067 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Penrith/Shap | KIRKBY STEPHEN | T12 | 33 | KIRKBY STEPHEN | 11 | Dy11 | 5 | 133 | 113.05 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Penrith/Shap | KIRKBY THORE | T11 | 33 | KIRKBY THORE | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Penrith/Shap | KIRKBY THORE | T12 | 33 | KIRKBY THORE | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Penrith/Shap | LITTLE SALKELD | T11 | 33 | LITTLE SALKELD | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Penrith/Shap | LITTLE SALKELD | T12 | 33 | LITTLE SALKELD | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Penrith/Shap | NEWBIGGIN ON LUNE | T11 | 33 | NEWBIGGIN ON LUNE | 11 | Dy11 | 21 | 256 | 217.6 | 5.72 | -17.16 | 3 | Full Capability | solid
Penrith/Shap | NEWBY | T11 | 33 | NEWBY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 6.35
Penrith/Shap | PENRITH BSP | T11 | 33 | PENRITH BSP | 11 | Dy11 | 4 | 100 | 85 | 17.1 | -5.7 | 11.5 / 23 | Full Capability | 6.35
Penrith/Shap | PENRITH BSP | T12 | 33 | PENRITH BSP | 11 | Dy11 | 4 | 100 | 85 | 17.1 | -5.7 | 11.5 / 23 | Full Capability | 6.35
Penrith/Shap | PENRITH BSP | T13 | 33 | PENRITH BSP | 11 | Dy11 | 4.95 | 110.4 | 93.84 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Penrith/Shap | SELSMIRE | T11 | 33 | SELSMIRE | 11 | Dy11 | 5 | 133 | 113.05 | 5 | -5 | 4 / 8 | Full Capability | solid
Penrith/Shap | SHAP GRID | T11 | 33 | SHAP PRIMARY | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | 6.35
Penrith/Shap | SHAP GRID | T12 | 33 | SHAP PRIMARY | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Penrith/Shap | SKELTON C | T11 | 33 | SKELTON C | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 7.5 | Full Capability | 6.35
Penrith/Shap | WHINFELL | T11 | 33 | WHINFELL | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.1 | 5 | Full Capability | 6.35
Preston East | AVENHAM | T11 | 33 | AVENHAM | 6.6 | Yx0* | 5.3 | 112.35 | 843 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.18
Preston East | AVENHAM | T12 | 33 | AVENHAM | 6.6 | Yx0* | 5.31 | 112.96 | 843.19 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.18
Preston East | BUSHELL ST | T11 | 33 | BUSHELL ST | 6.6 | Yy0 | 4 | 110 | 150 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Preston East | CRAGGS ROW | T12 | 33 | CRAGGS ROW | 6.6 | Yy0 | 4 | 110 | 144 | 9.9 | -3.3 | 11.5 / 23 | Full Capability | 3.81
Preston East | DODGSON RD | T11 | 33 | DODGSON RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Preston East | DODGSON RD | T12 | 33 | DODGSON RD | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Preston East | LONGRIDGE | T11 | 33 | LONGRIDGE | 6.6 | Yy0 | 4 | 100 | 303 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Preston East | LONGRIDGE | T12 | 33 | LONGRIDGE | 6.6 | Yy0 | 4 | 100 | 303 | 6 | -17 | 11.5 / 23 | Full Capability | 3.81
Preston East | PRESTON EAST | T11 | 33 | PRESTON EAST | 6.6 | Yy0 | 4.4 | 87 | 517.77 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Preston East | PRESTON EAST | T12 | 33 | PRESTON EAST | 6.6 | Yy0 | 4.4 | 87 | 515.83 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Preston East | RIBBLETON | T11 | 33 | RIBBLETON | 6.6 | Yy0 | 4 | 100 | 92.48 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Preston East | RIBBLETON | T12 | 33 | RIBBLETON | 6.6 | Yy0 | 4 | 100 | 92.48 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Red Bank | ANCOATS NORTH | T11 | 33 | ANCOATS NORTH | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Red Bank | ANCOATS NORTH | T12 | 33 | ANCOATS NORTH | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Red Bank | ANCOATS NORTH | T14 | 33 | ANCOATS NORTH | 6.6 | Dx11 | 5.19 | 111 | 85 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Red Bank | BLACKLEY | T11 | 33 | BLACKLEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Red Bank | BLACKLEY | T12 | 33 | BLACKLEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Red Bank | CANNON ST | T11 | 33 | CANNON ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.7 | -17.2 | 10 / 20 | 11.5 / 12.9 | 3.81
Red Bank | CANNON ST | T12 | 33 | CANNON ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.7 | -17.2 | 10 / 20 | 11.5 / 12.9 | 3.81
Red Bank | CANNON ST | T13 | 33 | CANNON ST | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.7 | -17.2 | 10 / 20 | 11.5 / 12.9 | 3.81
Red Bank | HARPURHEY | T11 | 33 | HARPURHEY | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Red Bank | HARPURHEY | T12 | 33 | HARPURHEY | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Red Bank | STRANGEWAYS | T11 | 33 | STRANGEWAYS | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Red Bank | STRANGEWAYS | T12 | 33 | STRANGEWAYS | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
Ribble | ASHTON | T11 | 33 | ASHTON | 6.6 | Dz0 | 4 | 104 | 85 | 4.5 | -15 | 10 | Not Known | 3.81
Ribble | BAMBER BRIDGE | T11 | 33 | BAMBER BRIDGE | 11 | Dz0 | 4 | 104 | 306 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Ribble | BAMBER BRIDGE | T12 | 33 | BAMBER BRIDGE | 11 | Dz0 | 4 | 104 | 306 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Ribble | BLACKBULL | T11 | 33 | BLACKBULL | 6.6 | Yx0 | 5.18 | 112 | 652.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Ribble | BLACKBULL | T12 | 33 | BLACKBULL | 6.6 | Yx0 | 5.18 | 113 | 652.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Ribble | CATTERALL WATERWORKS | T11 | 33 | CATTERALL WATERWORKS | 6.6 | Yy0 | 5 | 133 | 399 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 3.81
Ribble | DOUGLAS ST | T11 | 33 | DOUGLAS ST | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Ribble | DOUGLAS ST | T12 | 33 | DOUGLAS ST | 6.6 | Yy0 | 4 | 100 | 297 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 3.81
Ribble | GARSTANG | T11 | 33 | GARSTANG | 6.6 | Ydy0 | 3.948 | 113.478 | 680.868 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Ribble | HOLME RD | T11 | 33 | HOLME RD | 11 | Yy0 | 4 | 100 | 300 | 10.6 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Ribble | HOLME RD | T12 | 33 | HOLME RD | 11 | Yy0 | 4 | 100 | 300 | 10.6 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Leyland | HIGHER WALTON | T11 | 33 | HIGHER WALTON | 11 | Yy0 | 4 | 100 | 297 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Leyland | HIGHER WALTON | T12 | 33 | HIGHER WALTON | 11 | Yy0 | 4 | 100 | 297 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Ribble | MOORSIDE | T11 | 33 | MOORSIDE | 6.6 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Ribble | MOORSIDE | T12 | 33 | MOORSIDE | 6.6 | Dz0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Ribble | ST MARYS ST | T11 | 33 | ST MARYS ST | 6.6 | Dz0 | 4 | 104 | 321 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Ribble | ST MARYS ST | T12 | 33 | ST MARYS ST | 6.6 | Dz0 | 4 | 104 | 309 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Ribble | TARDY GATE | T11 | 33 | TARDY GATE | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Ribble | TARDY GATE | T12 | 33 | TARDY GATE | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Ribble | TULKETH | T11 | 33 | TULKETH | 6.6 | Yy0 | 4 | 100 | 288 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Ribble | TULKETH | T12 | 33 | TULKETH | 6.6 | Yy0 | 4 | 100 | 285 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Rochdale Central | ROCHDALE CENTRAL PRY | T11 | 33 | ROCHDALE CENTRAL PRY | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 4.35
Rochdale Central | ROCHDALE CENTRAL PRY | T12 | 33 | ROCHDALE CENTRAL PRY | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 4.35
Rochdale Central | ROCHDALE CENTRAL PRY | T13 | 33 | ROCHDALE CENTRAL PRY | 6.6 | Yy0 | 4 | 100 | 300 | 4.5 | -15 | 11.5 / 23 | 4.61 | 3.81
Rochdale Central | SPOTLAND | T11 | 33 | SPOTLAND | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Rochdale Central | SPOTLAND | T12 | 33 | SPOTLAND | 6.6 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Rochdale Central | WHITWORTH | T11 | 33 | WHITWORTH | 6.6 | Yy0 | 5 | 133 | 399 | 5.7 | -17.2 | 4 / 8 | Full Capability | 3.81
Rochdale Central | WHITWORTH | T12 | 33 | WHITWORTH | 6.6 | Yy0 | 5 | 133 | 399 | 7.5 | -7.5 | 7.5 | Not Known | 3.81
Rossendale | GRANE RD | T11 | 33 | GRANE RD | 6.6 | Yy0 | 5 | 133 | 399 | 4.7 | -15 | 7.5 | Full Capability | 3.81
Rossendale | GRANE RD | T12 | 33 | GRANE RD | 6.6 | Yy0 | 5 | 133 | 399 | 4.7 | -15 | 7.5 | Full Capability | 3.81
Rossendale | HAREHOLME | T11 | 33 | HAREHOLME | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Rossendale | HAREHOLME | T12 | 33 | HAREHOLME | 6.6 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 3.81
Rossendale | PRINNY HILL | T11 | 33 | PRINNY HILL | 6.6 | Yy0 | 5 | 133 | 399 | 4.5 | -15 | 7.5 | Full Capability | 3.81
Rossendale | RAWTENSTALL RD | T11 | 33 | RAWTENSTALL RD | 6.6 | Yy0 | 5 | 115.13 | 1564.46 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Rossendale | RAWTENSTALL RD | T12 | 33 | RAWTENSTALL RD | 6.6 | Yy0 | 5.405 | 114.26 | 1564.46 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
Rossendale | STUBBINS | T11 | 33 | STUBBINS | 11 | Yy0 | 3 | 70 | 240 | 5.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Rossendale | STUBBINS | T12 | 33 | STUBBINS | 11 | Yy0 | 3 | 70 | 240 | 5.7 | -17.1 | 19 / 38 | Full Capability | 6.35
Rossendale | WESLEY PLACE BACUP | T11 | 33 | WESLEY PLACE BACUP | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Rossendale | WESLEY PLACE BACUP | T12 | 33 | WESLEY PLACE BACUP | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.2 | 11.5 / 23 | 4.97 | 3.81
Royton | HEYSIDE | T11 | 33 | HEYSIDE | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Royton | HEYSIDE | T12 | 33 | HEYSIDE | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Royton | ROYTON GRID | T11 | 33 | ROYTON GRID | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Royton | ROYTON GRID | T12 | 33 | ROYTON GRID | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Royton | SHAW | T11 | 33 | SHAW | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Royton | SHAW | T12 | 33 | SHAW | 6.6 | Dy11 | 3.952 | 117.391 | 99.783 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Royton | WILLOWBANK | T11 | 33 | WILLOWBANK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Royton | WILLOWBANK | T12 | 33 | WILLOWBANK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Sale | ASHTON ON MERSEY | T11 | 33 | ASHTON ON MERSEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Sale | ASHTON ON MERSEY | T12 | 33 | ASHTON ON MERSEY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Sale | BAGULEY | T11 | 33 | BAGULEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 10.48 / 10.49 | 6.3
Sale | BAGULEY | T12 | 33 | BAGULEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 10.48 / 10.49 | 6.3
West Didsbury | NORTHENDEN | T11 | 33 | NORTHENDEN | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
West Didsbury | NORTHENDEN | T12 | 33 | NORTHENDEN | 6.6 | Dy11 | 5.23 | 114 | 96.9 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Sale | SALE MOOR | T11 | 33 | SALE MOOR | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Sale | SALE PRIMARY | T11 | 33 | SALE PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Sale | SALE PRIMARY | T12 | 33 | SALE PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Sandgate | SANDGATE GRID | T11 | 33 | SANDGATE GRID | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Sandgate | SANDGATE GRID | T12 | 33 | SANDGATE GRID | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Siddick | SIDDICK | T11 | 33 | SIDDICK | 11 | Dx11 | 5.22 | 111.22 | 94.53 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Siddick | SIDDICK | T12 | 33 | SIDDICK | 11 | Dx11 | 5.22 | 111.22 | 94.53 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Skelmersdale | ORMSKIRK | T11 | 33 | ORMSKIRK | 11 | Yy0 | 4 | 100 | 300 | 5.8 | -17.2 | 11.5 / 23 | 5.06 | 6.32
Skelmersdale | ORMSKIRK | T12 | 33 | ORMSKIRK | 11 | Yy0 | 4 | 100 | 309 | 5.8 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Skelmersdale | PIMBO | T11 | 33 | PIMBO | 11 | Yy0 | 3 | 70 | 210 | 4.3 | -18.6 | 19 / 30 | 8.42 | 6.35
Skelmersdale | PIMBO | T12 | 33 | PIMBO | 11 | Yy0 | 3 | 70 | 210 | 4.3 | -18.6 | 19 / 30 | 8.42 | 6.35
Skelmersdale | SCARISBRICK | T11 | 33 | SCARISBRICK | 11 | Yy0 | 5 | 133 | 399 | 5.7 | -17.1 | 7.5 | Full Capability | 6.35
Skelmersdale | SKELMERSDALE GRID | T11 | 33 | SKELMERSDALE GRID | 11 | Yy0 | 4 | 100 | 297 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Skelmersdale | SKELMERSDALE GRID | T12 | 33 | SKELMERSDALE GRID | 11 | Yy0 | 4 | 100 | 312 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Skelmersdale | WILLOW HEY | T11 | 33 | WILLOW HEY | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Skelmersdale | WILLOW HEY | T12 | 33 | WILLOW HEY | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Spadeadam | ASKERTON CASTLE | T11 | 33 | ASKERTON CASTLE | 11 | Dy11 | 5 | 150 | 127.5 | 2.5 | -7.5 | 3 | Full Capability | solid
Spadeadam | EASTON | T11 | 33 | EASTON | 11 | Dy11 | 5 | 150 | 127.5 | 2.5 | -7.5 | 2 | Not Known | solid
Spadeadam | KINKRY HILL | T11 | 33 | KINKRY HILL | 11 | Dy11 | 21 | 256 | 217.6 | 5.72 | -17.16 | 3 | Full Capability | solid
Spadeadam | SPADEADAM | T11 | 33 | SPADEADAM | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | 9.2
Stainburn | ANNIE PIT | T11 | 33 | ANNIE PIT | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Stainburn | ANNIE PIT | T12 | 33 | ANNIE PIT | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 6.35
Stainburn | ASPATRIA | T11 | 33 | ASPATRIA | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 | Full Capability | 6.35
Stainburn | ASPATRIA | T12 | 33 | ASPATRIA | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 | Full Capability | 6.35
Stainburn | EMBLETON | T11 | 33 | EMBLETON | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Stainburn | EMBLETON | T12 | 33 | EMBLETON | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Stainburn | HDA NO1 | T11 | 33 | HDA NO1 | 11 | Dy11 | 5.5256 | 115.565 | 125.064 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Stainburn | HDA NO2 | T12 | 33 | HDA NO2 | 11 | Dy11 | 5.32 | 114 | 96.9 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Stainburn | KESWICK | T11 | 33 | KESWICK | 11 | Dy11 | 8.8144 | 114.733 | 97.5233 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Stainburn | LEYLAND NATIONAL | T11 | 33 | LEYLAND NATIONAL | 11 | Dy11 | 4 | 100 | 85 | 6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Stainburn | LEYLAND NATIONAL | T12 | 33 | LEYLAND NATIONAL | 11 | Dy11 | 4 | 100 | 85 | 6 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Stainburn | MARYPORT | T11 | 33 | MARYPORT | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Stainburn | MARYPORT | T12 | 33 | MARYPORT | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Stainburn | STAINBURN BSP | T11 | 33 | STAINBURN BSP | 11 | Dy11 | 5 | 133 | 113.05 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Stainburn | STAINBURN BSP | T12 | 33 | STAINBURN BSP | 11 | Dy11 | 5 | 133 | 113.05 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Stretford | CHESTER RD | T11 | 33 | CHESTER RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stretford | CHESTER RD | T12 | 33 | CHESTER RD | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Stretford | CHESTER RD | T13 | 33 | CHESTER RD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stretford | LONGFORD BRIDGE | T11 | 33 | LONGFORD BRIDGE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Stretford | LONGFORD BRIDGE | T12 | 33 | LONGFORD BRIDGE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.1 | 11.5 / 23 | Full Capability | 3.81
Stretford | MOSLEY RD | T11 | 33 | MOSLEY RD | 6.6 | Dy11 | 3.93 | 114.43 | 97.2655 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stretford | MOSLEY RD | T12 | 33 | MOSLEY RD | 6.6 | Dy11 | 3.95 | 114.52 | 97.342 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stretford | TRAFFORD | T11 | 33 | TRAFFORD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Stretford | TRAFFORD | T12 | 33 | TRAFFORD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.81
Stretford | URMSTON | T11 | 33 | URMSTON | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Stretford | URMSTON | T12 | 33 | URMSTON | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Stuart Street | ARDWICK | T11 | 33 | ARDWICK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Stuart Street | ARDWICK | T12 | 33 | ARDWICK | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Stuart Street | BRADFORD | T11 | 33 | BRADFORD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Stuart Street | BRADFORD | T13 | 33 | BRADFORD | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Stuart Street | CENTRAL MANCHESTER | T11 | 33 | CENTRAL MANCHESTER | 6.6 | Dy11 | 4.4 | 87 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Stuart Street | CENTRAL MANCHESTER | T12 | 33 | CENTRAL MANCHESTER | 6.6 | Dy11 | 4.4 | 87 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 3.81
Stuart Street | EASTLANDS | T11 | 33 | EASTLANDS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | EASTLANDS | T12 | 33 | EASTLANDS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | MONSALL PRIMARY | T11 | 33 | MONSALL PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | MONSALL PRIMARY | T12 | 33 | MONSALL PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | QUEENS PARK | T11 | 33 | QUEENS PARK | 6.6 | Dy11 | 4 | 102.9 | 86.7 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | QUEENS PARK | T13 | 33 | QUEENS PARK | 6.6 | Dy11 | 3.83 | 116.13 | 98.711 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Stuart Street | STUART ST PRIMARY | T11 | 33 | STUART ST PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Stuart Street | STUART ST PRIMARY | T12 | 33 | STUART ST PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
Thornton | COPSE RD | T11 | 33 | COPSE RD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Not Known | 3.81
Thornton | COPSE RD | T12 | 33 | COPSE RD | 6.6 | Yy0 | 4 | 100 | 300 | 5.7 | -17.1 | 11.5 / 23 | Not Known | 3.81
Thornton | GARSTANG | T12 | 33 | GARSTANG | 6.6 | Ydy0 | 3.93 | 114.22 | 685.3 | 4.5 | -15 | 11.5 / 23 | Full Capability | 3.81
Thornton | PREESALL | T11 | 33 | PREESALL | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Thornton | PREESALL | T12 | 33 | PREESALL | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Thornton | ROSSALL | T11 | 33 | ROSSALL | 6.6 | Ydy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Thornton | THORNTON PRY | T11 | 33 | THORNTON PRY | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Thornton | THORNTON PRY | T12 | 33 | THORNTON PRY | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Ulverston | ASKAM | T11 | 33 | ASKAM | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Ulverston | CONISTON | T11 | 33 | CONISTON | 11 | Dy11 | 5 | 133 | 113.05 | 5.7 | -17.2 | 4 / 8 | Full Capability | 6.35
Ulverston | DALTON | T12 | 33 | DALTON | 11 | Dy11 | 4 | 100 | 85 | 4.5 | -16.5 | 15 / 18.75 | Not Known | 6.35
Ulverston | GLAXO | T11 | 33 | GLAXO | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Ulverston | GLAXO | T12 | 33 | GLAXO | 11 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 6.35
Ulverston | GRANGE | T11 | 33 | GRANGE | 11 | Dy11 | 4 | 104 | 88.4 | 3 | -15 | 10 | Not Known | solid
Ulverston | GRANGE | T12 | 33 | GRANGE | 11 | Dy11 | 4 | 104 | 88.4 | 3 | -15 | 10 | Not Known | solid
Ulverston | HAVERTHWAITE | T11 | 33 | HAVERTHWAITE | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | solid
Ulverston | HAVERTHWAITE | T12 | 33 | HAVERTHWAITE | 11 | Dy11 | 5 | 133 | 113.05 | 4.5 | -15 | 7.5 | Not Known | solid
Ulverston | KIRKBY MOOR | T11 | 33 | KIRKBY MOOR | 11 | Dy11 | 5 | 133 | 113.05 | 5.2 | -4.9 | 7.5 | Full Capability | 6.35
Ulverston | ULVERSTON | T11 | 33 | ULVERSTON | 11 | Dx11 | 8.7541 | 111.733 | 94.9733 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Ulverston | ULVERSTON | T12 | 33 | ULVERSTON | 11 | Dx11 | 8.6774 | 112.067 | 95.2567 | 5.72 | -17.16 | 7.5 / 15 | Full Capability | 6.35
Vernon Park | HEATON MOOR | T11 | 33 | HEATON MOOR | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Vernon Park | HEATON MOOR | T12 | 33 | HEATON MOOR | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 3.81
Vernon Park | HEATON NORRIS | T11 | 33 | HEATON NORRIS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Vernon Park | HEATON NORRIS | T12 | 33 | HEATON NORRIS | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Not Known | 3.81
Vernon Park | PORTWOOD | T11 | 33 | PORTWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Vernon Park | PORTWOOD | T12 | 33 | PORTWOOD | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 6.35
Vernon Park | REDDISH VALE | T11 | 33 | REDDISH VALE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Vernon Park | REDDISH VALE | T12 | 33 | REDDISH VALE | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Vernon Park | ROMILEY | T11 | 33 | ROMILEY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Vernon Park | ROMILEY | T12 | 33 | ROMILEY | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Vernon Park | WOODLEY | T11 | 33 | WOODLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
Vernon Park | WOODLEY | T12 | 33 | WOODLEY | 11 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 6.35
West Didsbury | BENCHILL | T11 | 33 | BENCHILL | 11 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Full Capability | 6.3
West Didsbury | CHORLTON | T11 | 33 | CHORLTON | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.81
West Didsbury | DIDSBURY | T11 | 33 | DIDSBURY | 6.6 | Dy11 | 5.23 | 114 | 96.9 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
West Didsbury | DIDSBURY | T12 | 33 | DIDSBURY | 6.6 | Dy11 | 5.23 | 114 | 96.9 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
West Didsbury | WEST DIDSBURY PRIMARY | T11 | 33 | WEST DIDSBURY PRIMARY | 6.6 | Dy11 | 4 | 100 | 85 | 5.8 | -17.2 | 11.5 / 23 | Full Capability | 3.81
West Didsbury | WEST DIDSBURY PRIMARY | T12 | 33 | WEST DIDSBURY PRIMARY | 6.6 | Dy11 | 4.5 | 116 | 98.6 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.81
West Didsbury | WHALLEY RANGE | T11 | 33 | WHALLEY RANGE | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
West Didsbury | WHALLEY RANGE | T12 | 33 | WHALLEY RANGE | 6.6 | Dy11 | 4 | 100 | 85 | 4.5 | -18 | 15 / 21 | Not Known | 3.81
West Didsbury | WITHINGTON | T11 | 33 | WITHINGTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
West Didsbury | WITHINGTON | T12 | 33 | WITHINGTON | 6.6 | Dy11 | 4 | 104 | 88.4 | 4.5 | -15 | 10 / 14 | Not Known | 3.81
Westhoughton | CROWN LANE | T11 | 33 | CROWN LANE | 11 | Yy0 | 4 | 100 | 92.48 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Westhoughton | CROWN LANE | T12 | 33 | CROWN LANE | 11 | Yy0 | 4 | 100 | 92.48 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.35
Westhoughton | LOSTOCK | T11 | 33 | LOSTOCK | 11 | Yy0 | 4 | 100 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Westhoughton | LOSTOCK | T12 | 33 | LOSTOCK | 11 | Yy0 | 4 | 100 | 73.95 | 5.7 | -17.2 | 16 / 32 | Full Capability | 6.35
Westhoughton | WESTHOUGHTON GRID | T11 | 33 | WESTHOUGHTON GRID | 11 | Yy0 | 4 | 100 | 92.48 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Westhoughton | WESTHOUGHTON GRID | T12 | 33 | WESTHOUGHTON GRID | 11 | Yy0 | 4 | 100 | 92.48 | 5.7 | -17.2 | 11.5 / 23 | 5.06 | 6.35
Wigan | GIDLOW | T11 | 33 | GIDLOW | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 10.48 / 10.49 | 3.82
Wigan | GIDLOW | T12 | 33 | GIDLOW | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 10.48 / 10.49 | 3.82
Wigan | GREEN ST | T11 | 33 | GREEN ST | 6.6 | Dy11 | 4.48 | 114 | 96.9 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.82
Wigan | GREEN ST | T12 | 33 | GREEN ST | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | 11.5 / 12.9 | 3.82
Wigan | GREEN ST | T13 | 33 | GREEN ST | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.82
Wigan | KITT GREEN | T11 | 33 | KITT GREEN | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.82
Wigan | KITT GREEN | T12 | 33 | KITT GREEN | 6.6 | Dy11 | 4 | 100 | 85 | 5.7 | -17.2 | 11.5 / 23 | 11.5 / 13.11 | 3.82
Wigan | LAMBERHEAD | T11 | 33 | LAMBERHEAD | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.82
Wigan | LAMBERHEAD | T12 | 33 | LAMBERHEAD | 6.6 | Dy11 | 4 | 104 | 88.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 3.82
Wigan | UPHOLLAND | T11 | 33 | UPHOLLAND | 11 | Dz0 | 4 | 104 | 300 | 4.5 | -16.5 | 10 / 12.5 | Full Capability | 6.35
Wigan | UPHOLLAND | T12 | 33 | UPHOLLAND | 11 | Dz0 | 4 | 104 | 300 | 4.5 | -16.5 | 10 / 12.5 | Full Capability | 6.35
Wigan | WORSLEY MESNES | T11 | 33 | WORSLEY MESNES | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.82
Wigan | WORSLEY MESNES | T12 | 33 | WORSLEY MESNES | 6.6 | Dy11 | 4 | 100 | 85 | 4.3 | -18.6 | 11.5 / 23 | Not Known | 3.82
Wrightington | BOTANY BAY | T12 | 33 | BOTANY BAY | 11 | Yy0 | 4 | 100 | 92.48 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.32
Wrightington | BURSCOUGH BRIDGE | T11 | 33 | BURSCOUGH BRIDGE | 11 | Ydy0 | 4 | 104 | 288 | 4.5 | -15 | 10 / 12.5 | Not Known | 6.32
Wrightington | BURSCOUGH BRIDGE | T12 | 33 | BURSCOUGH BRIDGE | 11 | Dz0 | 4 | 104 | 309 | 4.5 | -15 | 10 / 12.5 | Not Known | 6.32
Wrightington | CHORLEY SOUTH | T11 | 33 | CHORLEY SOUTH | 11 | Yy0 | 4 | 100 | 285 | 4 | -12 | 11.5 / 23 | Full Capability | 6.35
Wrightington | CHORLEY SOUTH | T12 | 33 | CHORLEY SOUTH | 11 | Yy0 | 4 | 104 | 312 | 4.5 | -15 | 10 / 14 | Full Capability | 6.35
Wrightington | HANGING BRIDGE | T11 | 33 | HANGING BRIDGE | 11 | Yy0 | 5 | 133 | 399 | 5.7 | -17.2 | 7.5 / 15 | Full Capability | 6.35
Wrightington | STANDISH | T11 | 33 | STANDISH | 11 | Yy0 | 4.0474 | 111.435 | 891.478 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Wrightington | STANDISH | T12 | 33 | STANDISH | 11 | Yy0 | 4.047 | 111.435 | 891.478 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 6.35
Wrightington | TARLETON | T11 | 33 | TARLETON | 11 | Dz0 | 5.23 | 113.957 | 664.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Wrightington | TARLETON | T12 | 33 | TARLETON | 11 | Dz0 | 5.23 | 113.83 | 664.4 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Wrightington | WOODFIELD RD | T11 | 33 | WOODFIELD RD | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.32
Wrightington | WOODFIELD RD | T12 | 33 | WOODFIELD RD | 11 | Yy0 | 4 | 100 | 300 | 4.3 | -18.6 | 11.5 / 23 | 4.97 | 6.32
Wrightington | WRIGHTINGTON PRIMARY | T11 | 33 | WRIGHTINGTON PRIMARY | 11 | Ydy0 | 4.48 | 115 | 346.17 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Wrightington | WRIGHTINGTON PRIMARY | T12 | 33 | WRIGHTINGTON PRIMARY | 11 | Ydy0 | 4.49 | 115 | 347.7 | 5.72 | -17.16 | 11.5 / 23 | Full Capability | 6.35
Longsight | CIRCLE SQUARE | T12 | 33 | CIRCLE SQUARE | 6.6 | Dy11 | 4.083 | 111.739 | 94.978 | 5.7 | -17.2 | 11.5 / 23 | Full Capability | 3.81
Altrincham | MEDIPARK | T12 | 33 | MEDIPARK | 11 | Dx11 | 3.1 | 83.3 | 74.9 | 5.72 | -17.16 | 16 / 32 | Full Capability | 6.35
Notes
Transformer Ratings:- The ratings given in the above table indicate the nameplate rating of the transformers at each location.
The actual rating will depend on the required duty, load cycle, ambient temperature, system security and operational factors.
Disclaimer
The information contained in this Statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West Limited will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval, and payment of appropriate charges.
The information contained in this Statement is the Copyright of Electricity North West Limited, All Rights Reserved.

## 132kV TX Data Nov2024
TRANSFORMER DATA FOR 132kV SUBSTATIONS
GSP or S/S Group | Substation or busbar name |  |  |  | Vector Group | Positive Sequence Impedance |  | Zero Sequence Reactance | Tap |  | Transformer Name Plate Rating | Reverse Power Capability | Method of Earthing (HV neutrals all solid) | Earthing Details
| Node 1 | Voltage (kV) | Node 2 | Voltage (kV) |  | % on 100 MVA base |  | Xo | Maximum % | Minimum % | MVA | MVA | LV Earthing Impedance (Ohms) | LV Earthing Resistor (Amps)
[6 empty] | R | X
Bredbury | adswood 1 | 132 | adswood | 33 | Yd1 | 1.4 | 27.5 | 23.375 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Bredbury | adswood 2 | 132 | adswood | 33 | Yd1 | 1.3 | 25.6 | 21.76 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Kearsley | agecroft 1 | 132 | agecroft | 33 | Yd1 | 1.0395 | 28.9473 | 24.6211 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Kearsley | agecroft 2 | 132 | agecroft | 33 | Yd1 | 1.0626 | 28.8464 | 24.5361 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Carrington | altrincham 1 | 132 | altrincham | 33 | Yd1 | 0.7088 | 25.19 | 21.42 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Carrington | altrincham 2 | 132 | altrincham | 33 | Yd1 | 0.6981 | 24.8782 | 21.1548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | atherton 1 | 132 | atherton | 33 | Yd1 | 0.7734 | 23.2641 | 19.7855 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | atherton 2 | 132 | atherton | 33 | Yd1 | 0.7827 | 23.2088 | 19.7387 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Hutton | barrow 1 | 132 | barrow | 33 | Yd1 | 1.5693 | 27.5103 | 23.4217 | +10 | -20 | 60 | Full Capability | 19.05 | 1000
Hutton | barrow 2 | 132 | barrow | 33 | Yd1 | 1.4943 | 26.8464 | 22.8548 | +10 | -20 | 60 | Full Capability | 19.05 | 1000
Carrington | barton 1 | 132 | barton | 33 | Yd1 | 1.0272 | 29.0148 | 24.678 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Carrington | barton 2 | 132 | barton | 33 | Yd1 | 0.9208 | 20.6955 | 17.6086 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Carrington | barton 3 | 132 | barton | 33 | Yd1 | 0.76289 | 27.6561 | 25.597 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Rochdale | belfield 1 | 132 | belfield | 33 | Yd1 | 0.7216 | 25.6559 | 21.8161 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Rochdale | belfield 2 | 132 | belfield | 33 | Yd1 | 0.7456 | 25.5441 | 21.7218 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stanah | bispham 1 | 132 | bispham | 33 | Yd1 | 0.649 | 25.2687 | 21.4855 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stanah | bispham 2 | 132 | bispham | 33 | Yd1 | 0.5684 | 27.827 | 23.653 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Penwortham East | blackburn 1 | 132 | blackburn | 33 | Yd1 | 0.5648 | 24.6434 | 23.6 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Penwortham East | blackburn 2 | 132 | blackburn | 33 | Yd1 | 0.5875 | 27.77 | 23.77 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Stanah | blackpool 1 | 132 | blackpool | 33 | Yd1 | 0.6972 | 24.1229 | 20.513 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stanah | blackpool 2 | 132 | blackpool | 33 | Yd1 | 0.7012 | 27.457 | 23.3461 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
South Manchester | bloom street 1 | 132 | bloom street | 33 | Yd1 | 0.4216 | 25.9632 | 22.0716 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
South Manchester | bloom street 2 | 132 | bloom street | 33 | Yd1 | 0.4232 | 25.8965 | 22.015 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Kearsley | bolton 1 | 132 | bolton | 33 | Yd1 | 0.81944 | 20.7672 | 17.6658 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Kearsley | bolton 3 | 132 | bolton | 33 | Yd1 | 0.5691 | 28 | 23.7949 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Kearsley | bolton 4 | 132 | bolton | 33 | Yd1 | 0.5691 | 28 | 23.7949 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Rochdale | burnley 1 | 132 | burnley | 33 | Yd1 | 0.7246 | 25.5447 | 21.7218 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Rochdale | burnley 2 | 132 | burnley | 33 | Yd1 | 0.7271 | 25.6007 | 21.7693 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | bury1 | 132 | bury | 33 | Yd1 | 0.8185 | 25.3198 | 21.533 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | bury2 | 132 | bury | 33 | Yd1 | 0.8296 | 25.0973 | 21.3443 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stalybridge | buxton 1 | 132 | buxton | 33 | Yd1 | 0.729 | 24.8893 | 21.165 | +10 | -20 | 100 | Full Capability | 12.0972 | 1575
Stalybridge | buxton 2 | 132 | buxton | 33 | Yd1 | 0.6466 | 25.1027 | 21.3443 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Harker | carlise north | 132 | carlise north 1 | 11 | Ydy0 | 1.5 | 102 | 37.5 | +10 | -20 | 30 | Full Capability | 6.37 | 1000
Harker | carlise north | 133 | carlise north 2 | 11 | Ydy0 | 1.647 | 65.55 | 55.72 | +10 | -20 | 30 | Full Capability | 6.37 | 1000
Harker | carlisle 1 | 132 | carlisle | 33 | Yd1 | 0.57145 | 27.794 | 23.6429 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Harker | carlisle 2 | 132 | carlisle | 33 | Yd1 | 1.0591 | 24.4771 | 20.825 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Harker | carlisle 3 | 132 | carlisle | 33 | Yd1 | 1.0283 | 25.8456 | 21.9861 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Carrington | carrington 1 | 132 | carrington bsp | 33 | Yd1 | 1.2093 | 28.0406 | 23.8567 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Carrington | carrington 2 | 132 | carrington bsp | 33 | Yd1 | 1.2155 | 28.1237 | 23.9275 | +10 | -20 | 30 | Full Capability | 19.0531 | 1000
Rochdale | castleton 1 | 132 | castleton | 33 | Yd1 | 0.7284 | 27.4303 | 23.324 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Rochdale | castleton 2 | 132 | castleton | 33 | Yd1 | 0.5695 | 28.1052 | 23.8943 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | chadderton 1 | 132 | chadderton | 33 | Yd1 | 0.536 | 27.2717 | 23.1854 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | chadderton 2 | 132 | chadderton | 33 | Yd1 | 0.5343 | 25.5494 | 21.7218 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Rochdale | rochdale central 1 | 132 | rochdale central | 33 | Yd1 | 1.0555 | 21.9747 | 18.7 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Rochdale | rochdale central 2 | 132 | rochdale central | 33 | Yd1 | 1.0555 | 21.9747 | 18.7 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Stalybridge | droylsden 1 | 132 | droylsden | 33 | Yd1 | 0.6101 | 18.8561 | 16.0361 | +10 | -20 | 90 | Full Capability | 12.7021 | 1500
Stalybridge | droylsden 2 | 132 | droylsden | 33 | Yd1 | 0.5949 | 18.7125 | 15.9137 | +10 | -20 | 90 | Full Capability | 12.7021 | 1500
Harker | egremont 1 | 132 | egremont | 33 | Yd1 | 0.8055 | 23.5973 | 20.0694 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Harker | egremont 2 | 132 | egremont | 33 | Yd1 | 0.7925 | 23.4306 | 19.9274 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | frederick rd 1 | 132 | frederick rd | 33 | Yd1 | 0.9208 | 20.9127 | 17.7931 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Kearsley | frederick rd 2 | 132 | frederick rd | 33 | Yd1 | 1 | 20.6758 | 17.595 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Kearsley | frederick rd 3 | 132 | frederick rd | 33 | Yd1 | 0.9805 | 22.4116 | 19.068 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Bold | golborne 1 | 132 | golborne | 33 | Yd1 | 0.706 | 26.4566 | 22.4961 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Bold | golborne 2 | 132 | golborne | 33 | Yd1 | 0.7061 | 27.3239 | 23.233 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | greenhill 2 | 132 | greenhill | 33 | Yd1 | 0.6611 | 26.9359 | 22.9024 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | greenhill 3 | 132 | greenhill | 33 | Yd1 | 0.6544 | 26.5469 | 22.5717 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Bredbury | hazel grove 1 | 132 | hazel grove | 33 | Yd1 | 0.7407 | 24.989 | 21.25 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Bredbury | hazel grove 2 | 132 | hazel grove | 33 | Yd1 | 0.7432 | 24.8769 | 21.1548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stalybridge | hartshead 1 | 132 | heyrod | 33 | Yd1 | 0.9855 | 21.0269 | 17.8925 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Stalybridge | hartshead 2 | 132 | heyrod | 33 | Yd1 | 0.9722 | 21.0606 | 17.9205 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Stalybridge | hartshead 3 | 132 | heyrod | 33 | Yd1 | 0.9922 | 21.4431 | 18.2461 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Padiham | huncoat 1 | 132 | huncoat | 33 | Yd1 | 0.6396 | 32.7047 | 27.8043 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Padiham | huncoat 2 | 132 | huncoat | 33 | Yd1 | 0.6302 | 32.7939 | 27.88 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stalybridge | hyde1 | 132 | hyde | 33 | Yd1 | 0.565 | 27.9 | 23.715 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Stalybridge | hyde2 | 132 | hyde | 33 | Yd1 | 0.565 | 27.9 | 23.715 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Hutton | kendal 1 | 132 | kendal | 33 | Yd1 | 0.8 | 25.7536 | 21.9011 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Hutton | kendal 2 | 132 | kendal | 33 | Yd1 | 0.7961 | 25.6537 | 21.8161 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Heysham | lancaster 1 | 132 | lancaster | 33 | Yd1 | 0.8361 | 25.5413 | 21.7218 | +10 | -20 | 90 | Full Capability | 19.0531 | 1000
Heysham | lancaster 2 | 132 | lancaster | 33 | Yd1 | 0.8179 | 25.3198 | 21.533 | +10 | -20 | 90 | Full Capability | 19.0531 | 1000
Hutton | lancaster 3 | 132 | lancaster | 33 | Yd1 | 0.3854 | 32.042 | 29.067 | +10 | -20 | 90 | Full Capability | 19.0531 | 1000
Penwortham West | leyland 1 | 132 | leyland | 33 | Yd1 | 0.57 | 27.87 | 25.82 | +10 | -20 | 90 | Full Capability | 19.0531 | 1000
Penwortham West | leyland 2 | 132 | leyland | 33 | Yd1 | 0.57 | 27.89 | 25.82 | +10 | -20 | 90 | Full Capability | 19.0531 | 1000
Bredbury | longsight 1 | 132 | longsight | 33 | Yd1 | 0.568 | 27.661 | 23.512 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Bredbury | longsight 2 | 132 | longsight | 33 | Yd1 | 0.569 | 27.738 | 23.577 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Rochdale | lower darwen 1 | 132 | lower darwen | 33 | Yd1 | 0.7333 | 27.4342 | 23.3274 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Rochdale | lower darwen 2 | 132 | lower darwen | 33 | Yd1 | 0.7323 | 27.4342 | 23.3274 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Penwortham West | lytham 1 | 132 | lytham | 33 | Yd1 | 0.8 | 25.067 | 23.964 | +10 | -20 | 60 | Full Capability | 19.05 | 1000
Penwortham West | lytham 2 | 132 | lytham | 33 | Yd1 | 0.727 | 25.545 | 21.722 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
South Manchester | moss nook 1A | 132 | mossnook | 11 | Ydy0 | 2.988 | 98.8639 | 70.146 | +10 | -20 | 30 | Full Capability | 6.351 | 1000
South Manchester | moss nook 2B | 132 | mossnook | 33 | Yd1 | 1.0541 | 24.6104 | 20.938 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
South Manchester | moss nook 3 | 132 | mossnook | 33 | Yd1 | 0.9847 | 21.994 | 18.7136 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
South Manchester | moss nook 1B | 132 | mossnook | 33 | Yd1 | 1.0677 | 24.6429 | 20.9661 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Padiham | nelson 1 | 132 | nelson | 33 | Yd1 | 0.9333 | 25.4159 | 21.6181 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Rochdale | nelson 2 | 132 | nelson | 33 | Yd1 | 0.9347 | 25.616 | 21.788 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Stalybridge | newmills 1 | 132 | newmills | 33 | Yd1 | 1.2395 | 28.484 | 24.2343 | +10 | -20 | 45 | Full Capability | 24.2406 | 786
Stalybridge | newmills 2 | 132 | newmills | 33 | Yd1 | 1.2395 | 27.7493 | 23.6105 | +10 | -20 | 45 | Full Capability | 24.2406 | 786
Padiham | padiham 1 | 132 | padiham | 33 | Yd1 | 0.74444 | 27.5449 | 23.4217 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Padiham | padiham 2 | 132 | padiham | 33 | Yd1 | 0.7333 | 25.3224 | 21.533 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Penwortham West | peel 1 | 132 | peel | 33 | Yd1 | 1.276 | 28.6376 | 24.3661 | +10 | -20 | 45 | Full Capability | 24.1791 | 788
Penwortham West | peel 2 | 132 | peel | 33 | Yd1 | 1.2666 | 28.8162 | 24.5174 | +10 | -20 | 45 | Full Capability | 24.1791 | 788
Harker | penrith 1A | 132 | penrith | 33 | Yd1 | 1.05 | 28.55 | 24.28 | +10 | -20 | 60 | Full Capability | 12.7 | 1500
Harker | penrith 2A | 132 | penrith | 33 | Yd1 | 2.08 | 41.6681 | 37.498 | +10 | -20 | 60 | Full Capability | 12.7 | 1500
Penwortham East | Preston East 1 | 132 | Preston East | 33 | Yd1 | 1.3 | 25.6 | 21.76 | +10 | -20 | 90 | Full Capability | 18.2 | 1046
Penwortham East | Preston East 2 | 132 | Preston East | 33 | Yd1 | 1.3 | 25.6 | 21.76 | +10 | -20 | 90 | Full Capability | 18.2 | 1046
Washway Farm | Orrell 1 | 132 | Orrell | 33 | Yd1 | 0.56467 | 27.92 | 23.73 | +10 | -20 | 90 | Full Capability | 19.05 | 1050
Kirkby | Orrell 2 | 132 | Orrell | 33 | Yd1 | 0.56467 | 27.92 | 23.73 | +10 | -20 | 90 | Full Capability | 19.05 | 1050
Kearsley | radcliffe 1 | 132 | radcliffe | 11 | Yd1 | 2.6 | 66.4492 | 56.525 | +10 | -20 | 30 | Full Capability | 3.9694 | 1600
Kearsley | radcliffe 2 | 132 | radcliffe | 11 | Yd1 | 2.6288 | 66.6141 | 56.6661 | +10 | -20 | 30 | Full Capability | 3.9694 | 1600
Whitegate | redbank 2 | 132 | redbank | 33 | Yd1 | 0.766 | 23.0983 | 19.6443 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | redbank 3 | 132 | redbank | 33 | Yd1 | 0.7666 | 22.8752 | 19.4548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Penwortham East | ribble 1 | 132 | ribble | 33 | Yd1 | 0.758 | 27.4335 | 23.3274 | +10 | -20 | 90 | Full Capability | 19.05 | 1050
Penwortham East | ribble 2 | 132 | ribble | 33 | Yd1 | 0.7548 | 27.6667 | 23.5254 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Penwortham East | ribble 3 | 132 | ribble | 33 | Yd1 | 0.7407 | 26.2115 | 22.2887 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Fiddlers Ferry | risley 2 | 132 | risley | 11 | Yd1 | 2.0453 | 79.5737 | 67.66 | +10 | -20 | 30 | Full Capability | 4.0712 | 1560
Padiham | rossendale 1 | 132 | rossendale | 33 | Yd1 | 0.9888 | 27.8154 | 23.658 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Padiham | rossendale 2 | 132 | rossendale | 33 | Yd1 | 0.9813 | 27.6486 | 23.5161 | +10 | -20 | 90 | Full Capability | 19.5 | 1000
Whitegate | royton 1 | 132 | royton | 33 | Yd1 | 0.8723 | 24.8287 | 21.1174 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Whitegate | royton 2 | 132 | royton | 33 | Yd1 | 0.8533 | 24.8734 | 21.1548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Carrington | sale 1 | 132 | sale | 33 | Yd1 | 1.1996 | 28.1745 | 23.97 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Carrington | sale 2 | 132 | sale | 33 | Yd1 | 0.95861 | 28.1837 | 23.97 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Hutton | sandgate | 132 | sandgate | 33 | Yd1 | 0.9692 | 28.3001 | 24.0692 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Harker | shap | 132 | shap | 33 | Yd1 | 1.2444 | 29.4177 | 25.0274 | +10 | -20 | 45 | Full Capability | 38.1062 | 500
Harker | siddick | 132 | siddick | 33 | Yd1 | 1.0458 | 26.4794 | 22.525 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Washway Farm | skelmersdale 1 | 132 | skelmersdale | 33 | Yd1 | 0.7172 | 25.1898 | 21.42 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Washway Farm | skelmersdale 2 | 132 | skelmersdale | 33 | Yd1 | 0.7049 | 25.1901 | 21.42 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Harker | spadeadam 1 | 132 | spadeadam | 11 | Ydy0 | 3.04 | 63.5934 | 87 | +10 | -20 | 30 | Full Capability | 9.2 | 1000
Harker | spadeadam 2 | 132 | spadeadam | 11 | Ydy0 | 1.6822 | 65.6444 | 87 | +10 | -20 | 30 | Full Capability | 9.2 | 1000
Harker | stainburn 1 | 132 | stainburn | 33 | Yd1 | 0.565 | 27.9 | 23.715 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
Harker | stainburn 2 | 132 | stainburn | 33 | Yd1 | 0.565 | 27.9 | 23.715 | +10 | -20 | 90 | Full Capability | 19.05 | 1000
South Manchester | stretford 1 | 132 | stretford | 33 | Yd1 | 0.7832 | 30.8781 | 26.2548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
South Manchester | stretford 2 | 132 | stretford | 33 | Yd1 | 0.7738 | 30.8783 | 26.2548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Stalybridge | stuart street 1 | 132 | stuart street | 33 | Yd1 | 0.44 | 27.33 | 25.42 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Stalybridge | stuart street 2 | 132 | stuart street | 33 | Yd1 | 0.45 | 27.17 | 25.31 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Stanah | thornton 1 | 132 | thornton | 33 | Yd1 | 1.1697 | 27.7087 | 23.5733 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Stanah | thornton 2 | 132 | thornton | 33 | Yd1 | 1.1582 | 27.8926 | 23.7292 | +10 | -20 | 60 | Full Capability | 19.0531 | 1000
Heysham | trimpell 1 | 132 | trimpell | 11 | Yd1 | 1.4281 | 32.902 | 27.9931 | +10 | -20 | 45 | Full Capability | 15.8776 | 1200
Heysham | trimpell 2 | 132 | trimpell | 11 | Yd1 | 1.4242 | 32.6349 | 27.7661 | +10 | -20 | 45 | Full Capability | 15.8776 | 1200
Hutton | ulverston 1 | 132 | ulverston | 33 | Yd1 | 0.565 | 27.58 | 23.443 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Hutton | ulverston 2 | 132 | ulverston | 33 | Yd1 | 0.565 | 27.649 | 23.5 | +10 | -20 | 90 | Full Capability | 18.1458 | 1050
Bredbury | vernon park 3 | 132 | vernon park | 33 | Yd1 | 0.7395 | 24.877 | 21.1548 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Bredbury | vernon park 4 | 132 | vernon park | 33 | Yd1 | 0.7604 | 25.4326 | 21.6274 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
South Manchester | west didsbury 1 | 132 | west didsbury | 33 | Yd1 | 0.9488 | 22.0626 | 18.7705 | +10 | -20 | 60 | Full Capability | 19 | 1050
South Manchester | west didsbury 2 | 132 | west didsbury | 33 | Yd1 | 0.9272 | 22.0135 | 18.728 | +10 | -20 | 60 | Full Capability | 19 | 1050
South Manchester | west didsbury 3 | 132 | west didsbury | 33 | Yd1 | 0.9272 | 22.0135 | 18.728 | +10 | -20 | 60 | Full Capability | 18.1458 | 1050
Kearsley | westhoughton 1 | 132 | westhoughton | 33 | Yd1 | 0.6666 | 26.7687 | 22.7604 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Kearsley | westhoughton 2 | 132 | westhoughton | 33 | Yd1 | 0.6654 | 26.6577 | 22.6661 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Washway Farm | wigan 1 | 132 | wigan | 33 | Yd1 | 0.5702 | 27.65 | 23.5 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Washway Farm | wigan 2 | 132 | wigan | 33 | Yd1 | 0.6335 | 33.0049 | 28.0594 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Penwortham West | wrightington 1 | 132 | wrightington | 33 | Yd1 | 0.6963 | 25.4905 | 21.675 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Penwortham West | wrightington 2 | 132 | wrightington | 33 | Yd1 | 0.7006 | 25.4904 | 21.675 | +10 | -20 | 90 | Full Capability | 12.0972 | 1575
Notes
Transformer Ratings:- The ratings given in the above table indicate the nameplate rating of the transformers at each location.
The actual rating will depend on the required duty, load cycle, ambient temperature, system security and operational factors.
Disclaimer
The information contained in this Statement is provided for the sole purpose of allowing existing and potential customers to assess the capabilities of the electricity network and opportunities for changes in their use of the network or for connecting to it.
While all reasonable effort has been made to ensure the accuracy of the information, Electricity North West Limited will accept no liability for any loss or damage caused by the information not being accurate.
Actual changes in supply capacity for existing customers or new connections are subject to detailed assessment and approval, and payment of appropriate charges.
The information contained in this Statement is the Copyright of Electricity North West Limited, All Rights Reserved.